## UPS QPL V1_V2
PD_ID | ENERGY STAR Partner | Brand Name | Model Name | Model Number | Additional Model Information | Product Type | Power Conversion Mechanism | Minimum Configuration Tested Model Number | Active Output Power Rating Minimum Configuration (W) | Apparent Output Power Rating Minimum Configuration (VA) | Maximum Configuration Tested Model Number | Active Output Power Rating Maximum Configuration (W) | Apparent Output Power Rating Maximum Configuration (VA) | Topology | Topology and Product Type Combined | Application | Rated Input Voltage (V rms) | Rated Input Frequency (Hz) | Rated Output Voltage (V) | Rated Output Frequency (Hz) | Rack Mountable | Rack Mount Height (U) | Height (mm) | Width (mm) | Depth (mm) | Total Number of Outlets | Number of Battery Backup and Surge Protected Outlets | Number of Surge Protected Only Outlets | Normal Mode(s) Input Dependency Characteristic (ac) | Modular UPS | Number of Normal Modes | Default Normal Mode (ac) | Test Input Voltage (V rms) | Test Input Frequency (Hz) | Test Output Voltage (V) | Test Output Frequency (Hz) | Total Input Power in W at 0% Load Min Config Lowest Dependency (ac) | Total Input Power in W at 0% Load Min Config Highest Dependency (ac) | Efficiency at 25% Load Min Config Lowest Dependency (ac) | Efficiency at 25% Load Min Config Highest Dependency (ac) | Efficiency at 50% Load Min Config Lowest Dependency (ac) | Efficiency at 50% Load Min Config Highest Dependency (ac) | Efficiency at 75% Load Min Config Lowest Dependency (ac) | Efficiency at 75% Load Min Config Highest Dependency (ac) | Efficiency at 100% Load Min Config Lowest Dependency (ac) | Efficiency at 100% Load Min Config Highest Dependency (ac) | Weighted Efficiency Calc Min Config Lowest Dependency | Weighted Efficiency Calc Min Config Highest Dependency | Total Input Power in W at 0% Load Minimum Configuration (dc) | Efficiency at 30% Load Minimum Configuration (dc) | Efficiency at 40% Load Minimum Configuration (dc) | Efficiency at 50% Load Minimum Configuration (dc) | Efficiency at 60% Load Minimum Configuration (dc) | Efficiency at 70% Load Minimum Configuration (dc) | Efficiency at 80% Load Minimum Configuration (dc) | Minimum Configuration Input Power Factor Lowest-Input Dependency | Minimum Configuration Input Power Factor Highest-Input Dependency | Total Input Power in W at 0% Load Max Config Lowest Dependency (ac) | Total Input Power in W at 0% Load Max Config Highest Dependency (ac) | Efficiency at 25% Load Max Config Lowest Dependency (ac) | Efficiency at 25% Load Max Config Highest Dependency (ac) | Efficiency at 50% Load Max Config Lowest Dependency (ac) | Efficiency at 50% Load Max Config Highest Dependency (ac) | Efficiency at 75% Load Max Config Lowest Dependency (ac) | Efficiency at 75% Load Max Config Highest Dependency (ac) | Efficiency at 100% Load Max Config Lowest Dependency (ac) | Efficiency at 100% Load Max Config Highest Dependency (ac) | Weighted Efficiency Calc Max Config Lowest Dependency | Weighted Efficiency Calc Max Config Highest Dependency | Total Input Power in W at 0% Load Maximum Configuration (dc) | Efficiency at 30% Load Maximum Configuration (dc) | Efficiency at 40% Load Maximum Configuration (dc) | Efficiency at 50% Load Maximum Configuration (dc) | Efficiency at 60% Load Maximum Configuration (dc) | Efficiency at 70% Load Maximum Configuration (dc) | Efficiency at 80% Load Maximum Configuration (dc) | Maximum Configuration Input Power Factor Lowest-Input Dependency | Maximum Configuration Input Power Factor Highest-Input Dependency | Efficiency (%) | Modular UPS Module Tested Model Number | Energy Storage Mechanism | Energy Storage System Technology | Energy Storage System Configuration | Energy Storage System Removable to Another Room | Energy Storage System 100% | Energy Storage System 50% | Energy Storage System Warranty | Energy Storage System Information URL | Battery Recycling URL | Network Connections Available | Communication Protocols | Communication Protocol Other | Manufacturer Take Back Program | Manufacturer Take Back Program URL | Model Web Page URL | Test Method Guidelines | Date Available on Market | Date Qualified | Markets | ENERGY STAR Model Identifier
2232858 | ADI | W BOX | 0E-350V6 | 0E-350V6 |  | Ac-output UPS | Static | CP350SLG | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.92 |  | 94.1 |  | 96.6 |  | 97.5 |  | 97.6 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | CP350SLG | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | N/A | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2015-01-30 | 2015-02-04 | United States, Canada | ES_1130837_0E-350V6_02092015080025_8825763
2233051 | ADI | W BOX | 0E-625V8LCD | 0E-625V8LCD |  | Ac-output UPS | Static | EC650LCD | 390 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 78 | 269 | 149 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.38 |  | 96.4 |  | 97.9 |  | 98.9 |  | 97.4 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | EC650LCD | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2015-01-30 | 2015-02-03 | United States, Canada | ES_1130837_0E-625V8LCD_02132015055930_7170034
2233250 | ADI | W BOX | 0E-1500V8VRD | 0E-1500V8VRD |  | Ac-output UPS | Static | 0E-1500V8VRD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 102-138 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.8 |  | 98.5 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.adiglobal.us/ | N/A | 2012-07-04 | 2015-02-12 | United States | ES_1130837_0E-1500V8VRD_02182015122555_70023788
2233251 | ADI | W BOX | 0E-1000V9VRD | 0E-1000V9VRD |  | Ac-output UPS | Static | 0E-1000V9VRD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 114-126 | 60-61 | No |  | 225 | 110 | 260 | 9 | 5 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.94 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.7 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 1 | 6 | 1 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.adiglobal.us/ | N/A | 2009-01-15 | 2015-02-12 | United States | ES_1130837_0E-1000V9VRD_02182015122555_70023788
2233952 | ADI | W BOX | 0E-825V12VRD | 0E-825V12VRD |  | Ac-output UPS | Static | AVRG900LCD | 480 | 825 |  |  |  | Other | ac - Other | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 177 | 309 | 88 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.86 |  | 95.9 |  | 97.6 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-01-29 | 2015-02-04 | United States | ES_1130837_0E-825V12VRD_02262015023947_8387165
2320493 | ADI | W BOX | 0E-RCKMT1000 | 0E-RCKMT1000 |  | Ac-output UPS | Static | OR1000PFCRT2U | 700 | 1000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 433 | 88 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.28 |  | 96.8 |  | 97.7 |  | 97.8 |  | 96.8 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 1 | N/A |  | Serial Port,Other,USB Port | None |  | Yes |  | N/A | N/A | 2018-07-01 | 2018-05-10 | United States, Canada | ES_1130837_0E-RCKMT1000_05262018075848_1528995
2320494 | ADI | W BOX | 0E-RCKMT1500 | 0E-RCKMT1500 |  | Ac-output UPS | Static | OR1500PFCRT2U | 1050 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 433 | 88 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.18 |  | 97.4 |  | 97.4 |  | 96.9 |  | 96.3 |  | 96.8 | [8 empty] | 0.99 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 1 | N/A |  | Serial Port,Other,USB Port | None |  | Yes |  | N/A | N/A | 2018-07-01 | 2018-05-10 | United States, Canada | ES_1130837_0E-RCKMT1500_05262018080435_1875873
2220809 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K2U700C | S4K2U700C |  | Ac-output UPS | Static | S4K2U700C | 630 | 700 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.6 |  | 83.5 |  | 88.5 |  | 89.6 |  | 89.8 |  | 89.3 | [8 empty] | 0.99 |  | 0.89 | 0.89 | [19 empty] | 89.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 11 | 27 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2009-09-20 | 2014-08-26 | United States, Canada | ES_1129526_S4K2U700C_09302014194903_6543437
2220810 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K2U1000C | S4K2U1000C |  | Ac-output UPS | Static | S4K2U1000C | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.71 |  | 84.6 |  | 88.6 |  | 88.9 |  | 88.4 |  | 88.7 | [8 empty] | 0.99 | [22 empty] | 88.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 17 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2009-09-20 | 2014-08-26 | United States, Canada | ES_1129526_S4K2U1000C_09222014104113_2473465
2220811 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K2U1500C | S4K2U1500C |  | Ac-output UPS | Static | S4K2U1500C | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 47.57 |  | 84.9 |  | 89 |  | 90.1 |  | 90 |  | 89.7 | [8 empty] | 0.99 | [22 empty] | 89.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2009-09-20 | 2014-08-26 | United States, Canada | ES_1129526_S4K2U1500C_09222014104457_2697528
2220812 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K2U2000C | S4K2U2000C |  | Ac-output UPS | Static | S4K2U2000C | 1746 | 1940 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.32 |  | 86.7 |  | 89.8 |  | 90.1 |  | 89.6 |  | 89.9 | [8 empty] | 0.99 | [22 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2009-09-20 | 2014-08-26 | United States, Canada | ES_1129526_S4K2U2000C_09222014104809_2889663
2220813 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K2U3000C | S4K2U3000C |  | Ac-output UPS | Static | S4K2U3000C | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 68.83 |  | 87.2 |  | 89.9 |  | 89.9 |  | 89.2 |  | 89.7 | [8 empty] | 0.99 | [22 empty] | 89.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2009-09-02 | 2014-08-26 | United States, Canada | ES_1129526_S4K2U3000C_09222014110425_3865353
2220814 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K4U6000C | S4K4U6000C | ,,S4K4U6000W0BATC and S4K144INTBATC; ,S4K4U6000W0BATC and S4K144INTBATC,S4K4U6000W0BATC and S4K144INTBATC | Ac-output UPS | Static | S4K4U6000C | 4800 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 4 | 173 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 82.9 |  | 90.2 |  | 92.6 |  | 92.9 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 13 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2010-04-09 | 2014-08-26 | United States, Canada | ES_1129526_S4K4U6000C_09222014111728_4648118
2220839 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S4K6U10KC | S4K6U10KC | ,S4K6U10KW0BATC and S4K288INTBATC, | Ac-output UPS | Static | S4K6U10KC | 9000 | 10000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 6 | 261 | 430 | 672 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 121.57 |  | 91.1 |  | 92.5 |  | 92.4 |  | 91.6 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 14 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2010-03-05 | 2014-08-26 | United States, Canada | ES_1129526_S4K6U10KC_09222014112641_5201630
2222296 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCB Series | S5Kbcdefghijklm (b=B; cde= 05A, 10A, 15A, 20A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N, 1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T, U or W; k=N, 1,2,3,4,5,6,7,8,9,A,B,C, or D; l=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | AS2A1NCUDNNX000 | 4500 | 5000 | AS2D1NCXDNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.6 |  | 87.5 |  | 91.5 |  | 92.6 |  | 93.1 |  | 92.4 | [8 empty] | 0.91 |  | 309.3 |  | 89.1 |  | 92.5 |  | 93.3 |  | 93.6 |  | 91.9 | [8 empty] | 0.95 | 0.95 | 92.4 | AS2A1NCUDNNX000, AS2D1NCXDNNX000 | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_09302014224607_7167518
2222483 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCC Series | S5Kbcdefghijklm (b=C; cde=10A, 15A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N,1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T,U or W; k=N,1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C, or D; l=N,1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | AS3B1NCVDNNX000 | 9000 | 10000 | AS3C1NCWDNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 100-240 | 50-60 | Yes | 24 | 1060 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 271.08 |  | 86.5 |  | 90.9 |  | 91.6 |  | 91.9 |  | 91.5 | [8 empty] | 0.98 |  | 324.88 |  | 88.3 |  | 91.4 |  | 92 |  | 92 |  | 90.8 | [8 empty] | 0.99 | 0.99 | 91.5 | AS3B1NCVDNNX000 AS3C1NCWDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_10142014161022_3022626
2222639 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCD Series | S5Kbcdefghijklm (b=D; cde= 10A, 15A, 20A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N, 1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T,U or W; k=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C, or D; l=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | AS4B1NCVDNNX000 | 9000 | 10000 | AS4D1NCXDNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 100-240 | 50-60 | No |  | 1240 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 278.53 |  | 86 |  | 90.3 |  | 91.3 |  | 91.6 |  | 91.1 | [8 empty] | 0.99 |  | 414.4 |  | 88.1 |  | 91.3 |  | 91.7 |  | 91.7 |  | 90.6 | [8 empty] | 0.98 | 0.98 | 91.1 | AS4B1NCVDNNX000 AS4D1NCXDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_10172014204707_8827943
2222640 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCE Series | S5Kbcdefghijklm (b=E; cde= 05A, 10A, 15A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N, 1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T,U or W; k=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C, or D; l=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | AS5A1NCUGNNX000 | 4500 | 5000 | AS5C1NCWGNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 16 | 695 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 134.06 |  | 86.1 |  | 89.9 |  | 90.6 |  | 90.6 |  | 90.4 | [8 empty] | 0.99 |  | 304.84 |  | 87.9 |  | 90.7 |  | 91.1 |  | 90.9 |  | 90.1 | [8 empty] | 0.99 | 0.99 | 90.4 | AS5A1NCUGNNX000 AS5C1NCWGNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_10172014205652_9412866
2222641 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCF Series | S5Kbcdefghijklm (b=F; cde= 05A, 10A, 15A, 20A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N, 1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T,U or W; k=N,1,2,3,4,5,6,7,8,9,A,B,C, or D; l=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | AS6A1NCUGNNX000 | 4500 | 5000 | AS6D1NCXGNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 125.5 |  | 86.3 |  | 90.3 |  | 90.8 |  | 90.8 |  | 90.6 | [8 empty] | 0.99 |  | 403 |  | 88.5 |  | 91.1 |  | 91.3 |  | 91 |  | 90.5 | [8 empty] | 0.99 | 0.99 | 90.6 | AS6A1NCUGNNX000, AS6D1NCXGNNX000 | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_10172014210255_9775990
2222901 | Appleton Grp LLC d/b/a Appleton Group | Emerson Industrial Automation | SOLAHD S5KCA Series | S5Kbcdefghijklm (b=A; cde= 05A, 10A, 15A, or NNN; f=N or A; g=N, R, or F; h=N or C; i=N, 1, 2, 3, 4, 5, 6, 7; j=A,B,C,D,E,F,G,H,J,K,L,M,N,P,Q,R,S,T, U or W; k=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C, or D; l=N, 1, 2, 3, 4, 5, 6, 7, 8, 9, A, B, C or D; m=C) |  | Ac-output UPS | Static | S5KA05ANNC1_NNC | 4500 | 5000 | S5KA15ANRC3_NNC | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 16 | 695 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.4 |  | 87.4 |  | 91.7 |  | 92.9 |  | 93.4 |  | 92.7 | [8 empty] | 0.91 |  | 242 |  | 88.8 |  | 92.3 |  | 93.2 |  | 93.6 |  | 91.7 | [8 empty] | 0.94 | 0.94 | 92.7 | S5KA05ANNC1_NNC, S5KA15ANRC3_NNC | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonindustrial.com/en-US/egselectricalgroup/products/control-power-solutions/power-protection-conditioning/uninterruptible-power-systems/Pages/default.aspx | N/A | 2013-09-12 | 2014-08-26 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1129526_S5Kbcdefghijklm_10212014165318_0398729
2323379 | Bxterra Power Technology | bXterra | BG450 | BG450 |  | Ac-output UPS | Static | BG450 | 255 | 450 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.68 |  | 96 |  | 97.6 |  | 98.1 |  | 98.3 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BG450_07192018235732_7353595
2323380 | Bxterra Power Technology | bXterra | BG550 | BG550 |  | Ac-output UPS | Static | BG550 | 330 | 550 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.67 |  | 96.6 |  | 97.9 |  | 98.4 |  | 98.5 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BG550_07192018234933_3069486
2323381 | Bxterra Power Technology | bXterra | BM850AVRLCD | BM850AVRLCD |  | Ac-output UPS | Static | BM850AVRLCD | 480 | 850 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.01 |  | 95.6 |  | 97.4 |  | 97.8 |  | 97.8 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BM850AVRLCD_07192018233827_1612275
2323383 | Bxterra Power Technology | bXterra | BM1000AVRLCD | BM1000AVRLCD |  | Ac-output UPS | Static | BM1000AVRLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.92 |  | 96.4 |  | 97.6 |  | 97.8 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BM1000AVRLCD_07192018232824_5419276
2323384 | Bxterra Power Technology | bXterra | BM1350AVRLCD | BM1350AVRLCD |  | Ac-output UPS | Static | BM1350AVRLCD | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 101 | 406 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.48 |  | 97.2 |  | 97.9 |  | 97.9 |  | 97.6 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 11 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BM1350AVRLCD_07192018231930_9910898
2323385 | Bxterra Power Technology | bXterra | BM1500AVRLCD | BM1500AVRLCD |  | Ac-output UPS | Static | BM1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 101 | 406 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.73 |  | 97.3 |  | 97.9 |  | 97.8 |  | 97.5 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 11 | 3 | https://www.bxterra.com/ups-battery-replacements/ |  | USB Port | None |  | No |  | https://www.bxterra.com/shop/ | N/A | 2018-08-13 | 2018-07-26 | United States, Canada | ES_1141975_BM1500AVRLCD_07192018225956_4632676
2323968 | Bxterra Power Technology | bXterra | SP1000LCDRT2U | SP1000LCDRT2U | SP1000LCDRTXL2U,SP1000LCDRTXL2U, | Ac-output UPS | Static | SP1000LCDRT2U | 990 | 1000 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 438 | 410 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 15.6 |  | 97.1 |  | 97.6 |  | 97.4 |  | 97.1 |  | 97.4 | [8 empty] | 1 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | Http://www.bxterra.com | N/A | 2018-07-25 | 2018-07-30 | United States, Canada | ES_1141975_SP1000LCDRT2U_08062018110013_9846295
2323969 | Bxterra Power Technology | bXterra | SP1500LCDRT2U | SP1500LCDRT2U | SP1500LCDRTXL2U,SP1500LCDRTXL2U, | Ac-output UPS | Static | SP1500LCDRT2U | 1350 | 1440 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 88 | 438 | 510 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 13.9 |  | 97.5 |  | 97.9 |  | 97.6 |  | 97.1 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | Http://www.bxterra.com | N/A | 2018-07-25 | 2018-07-30 | United States, Canada | ES_1141975_SP1500LCDRT2U_08062018111209_8954558
2323970 | Bxterra Power Technology | bXterra | SP2200LCDRT2U | SP2200LCDRT2U | SP2200LCDRTXL2U,SP2200LCDRTXL2U, | Ac-output UPS | Static | SP2200LCDRT2U | 1920 | 1920 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 88 | 438 | 630 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 14.6 |  | 97.8 |  | 97.8 |  | 97.4 |  | 97 |  | 97.4 | [8 empty] | 1 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | Http://www.bxterra.com | N/A | 2018-07-25 | 2018-07-30 | United States, Canada | ES_1141975_SP2200LCDRT2U_08062018111655_7647478
2323971 | Bxterra Power Technology | bXterra | SP3000LCDRT2U | SP3000LCDRT2U | SP3000LCDRTXL2U,SP3000LCDRTXL2U, | Ac-output UPS | Static | SP3000LCDRT2U | 2700 | 2880 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 88 | 438 | 630 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.1 |  | 98.2 |  | 97.8 |  | 97.3 |  | 96.5 |  | 97.2 | [8 empty] | 1 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | Http://www.bxterra.com | N/A | 2018-07-25 | 2018-07-30 | United States, Canada | ES_1141975_SP3000LCDRT2U_08062018112137_5485945
2330333 | Bxterra Power Technology | bXterra | BG350 | BG350 |  | Ac-output UPS | Static | BG350 | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 109 | 81 | 198 | 6 | 3 | 3 | Voltage and Frequency Dependent | Yes | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.59 |  | 96 |  | 98 |  | 98.6 |  | 98.8 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | BG350 | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 6 | 3 | N/A |  | None | None |  | Yes |  | https://www.bxterra.com/ | N/A | 2018-11-30 | 2018-11-20 | United States, Canada | ES_1141975_BG350_11282018161136_3466613
2304465 | CyberPower Systems, Inc. | amazonbasics | ABST400 | ABST400 |  | Ac-output UPS | Static | ABST400 | 255 | 400 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 82 | 110 | 184 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.18 |  | 96.8 |  | 98.1 |  | 98.6 |  | 98.8 |  | 98.3 | [31 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 6.9 | 1 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2017-12-01 | 2017-10-02 | United States, Canada | ES_1095904_ABST400_10032017025605_9365401
2304466 | CyberPower Systems, Inc. | amazonbasics | ABST600 | ABST600 |  | Ac-output UPS | Static | ABST600 | 360 | 600 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 80 | 155 | 272 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.34 |  | 97.4 |  | 98.4 |  | 98.8 |  | 98.8 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 1 | N/A |  | USB Port | None |  | Yes |  | N/A | N/A | 2017-12-01 | 2017-10-02 | United States, Canada | ES_1095904_ABST600_10032017025649_9409291
2330843 | CyberPower Systems, Inc. | amazonbasics | ABST800 | ABST800 |  | Ac-output UPS | Static | ABST800 | 450 | 800 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 80 | 178 | 310 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.9 |  | 97.5 |  | 98.5 |  | 98.7 |  | 98.8 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 1 | N/A |  | USB Port | Other | HID | No |  | https://www.amazon.com/AmazonBasics-Standby-UPS-800VA-Outlets/dp/B073Q3BSPG | N/A | 2018-12-01 | 2018-12-05 | United States, Canada | ES_1095904_ABST800_10032017025709_9429383
2031681 | CyberPower Systems, Inc. | CyberPower | CP1000AVRLCD | CP1000AVRLCD |  | Ac-output UPS | Static | CP1000AVRLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 60-61 | No |  | 225 | 110 | 260 | 9 | 5 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.94 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.7 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 1 | 6 | 1 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2009-01-15 | 2012-10-09 | United States | ES_1095904_CP1000AVRLCD_10102012051451_2559145
2073706 | CyberPower Systems, Inc. | CyberPower | CP850PFCLCD | CP850PFCLCD |  | Ac-output UPS | Static | CP850PFCLCD | 510 | 850 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 231 | 99 | 264 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.2 |  | 96.7 |  | 98.2 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 for CP850PFCLCD | 8 for CP850PFCLCD | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_CP850PFCLCD_10222012030059_999999
2073707 | CyberPower Systems, Inc. | CyberPower | CP1000PFCLCD | CP1000PFCLCD |  | Ac-output UPS | Static | CP1000PFCLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 231 | 99 | 264 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 96.5 |  | 98.1 |  | 98.4 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 for CP1500PFCLCD | 9 for CP1000PFCLCD | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_CP1000PFCLCD_10222012030059_999999
2073708 | CyberPower Systems, Inc. | CyberPower | CP1350PFCLCD | CP1350PFCLCD |  | Ac-output UPS | Static | CP1350PFCLCD | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.5 |  | 98.5 |  | 98.7 |  | 98.8 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 for CP1000PFCLCD | 9 for CP1350PFCLCD | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_CP1350PFCLCD_10222012030059_999999
2073709 | CyberPower Systems, Inc. | CyberPower | CP1500PFCLCD | CP1500PFCLCD |  | Ac-output UPS | Static | CP1500PFCLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.8 |  | 98.5 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 for CP1350PFCLCD | 11 for CP1500PFCLCD | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_CP1500PFCLCD_10222012030059_999999
2107072 | CyberPower Systems, Inc. | CyberPower | PR750LCD | PR750LCD |  | Ac-output UPS | Static | PR750LCD | 525 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 75-154 | 47-63 | 120-120 | 47-63 | No |  | 162 | 349 | 138 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.4 |  | 97.6 |  | 97.2 |  | 97.8 |  | 98 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 for PR750LCD | 15 for PR750LCD | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-14 | 2012-06-15 | United States | ES_1095904_ PR750LCD11072012124044_2563760
2107076 | CyberPower Systems, Inc. | CyberPower | PR2200LCD | PR2200LCD |  | Ac-output UPS | Static | PR2200LCD | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 163-286 | 47-63 | 120-120 | 47-63 | No |  | 433 | 198 | 513 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 16.4 |  | 97 |  | 97.8 |  | 97.8 |  | 97.5 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 8 for PR2200LCD | 26 for PR2200LCD | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-09-28 | 2012-09-28 | United States | ES_1095904_PR2200LCD11072012124044_2563760
2107077 | CyberPower Systems, Inc. | CyberPower | PR3000LCD | PR3000LCD |  | Ac-output UPS | Static | PR3000LCD | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 163-286 | 47-63 | 120-120 | 47-63 | No |  | 433 | 198 | 513 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 16.8 |  | 97.8 |  | 97.8 |  | 97.7 |  | 97.3 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 6 for PR3000LCD | 17 for PR3000LCD | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-09-28 | 2012-09-28 | United States | ES_1095904_PR3000LCD11072012124044_2563760
2118178 | CyberPower Systems, Inc. | CyberPower | CP750LCD, CP750LCDM | CP750LCD, CP750LCDM |  | Ac-output UPS | Static | CP750LCD | 420 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 120-120 | 47-63 | No |  | 83 | 165 | 278 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 96.7 |  | 97.8 |  | 97.4 |  | 98.3 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 10 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP750LCD, CP750LCDM_11082012052430_2563748
2118179 | CyberPower Systems, Inc. | CyberPower | CP425G, CP425Ga, CP425SLG, CP425HG, CP425HGa | CP425G, CP425Ga, CP425SLG, CP425HG, CP425HGa |  | Ac-output UPS | Static | CP425HG | 255 | 425 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 93.4 |  | 96.7 |  | 97.8 |  | 98 |  | 96.7 | [8 empty] | 1 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 7 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP425G_11082012052430_2563748
2118180 | CyberPower Systems, Inc. | CyberPower | CP500HG, CP500HGa | CP500HG, CP500HGa |  | Ac-output UPS | Static | CP500HG | 300 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 95 |  | 97.2 |  | 98 |  | 98.3 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP500HG, CP500HGa_11082012052430_2563748
2118181 | CyberPower Systems, Inc. | CyberPower | CP550SLG, CP550HG, CP550HGa | CP550SLG, CP550HG, CP550HGa |  | Ac-output UPS | Static | CP550HG | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.4 |  | 95 |  | 97.7 |  | 98.3 |  | 98.5 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP550SLG, CP550HG, CP550HGa_11082012052430_2563748
2118182 | CyberPower Systems, Inc. | CyberPower | CP600LCD | CP600LCD |  | Ac-output UPS | Static | CP600LCD | 340 | 600 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-140 | 57-63 | 120-120 | 57-63 | No |  | 83 | 165 | 278 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.8 |  | 96.4 |  | 97.7 |  | 98.2 |  | 98.3 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 9 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP600LCD_11082012052430_2563748
2118183 | CyberPower Systems, Inc. | CyberPower | CP625HG, CP625HGa | CP625HG, CP625HGa |  | Ac-output UPS | Static | CP625HG | 375 | 625 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 120-120 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.4 |  | 95.6 |  | 97.5 |  | 98.3 |  | 98.5 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP625HG, CP625HGa_11082012052430_2563748
2118184 | CyberPower Systems, Inc. | CyberPower | CP825LCD | CP825LCD |  | Ac-output UPS | Static | CP825LCD | 450 | 825 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-140 | 57-63 | 120-120 | 57-63 | No |  | 83 | 165 | 278 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.8 |  | 97.6 |  | 98.3 |  | 98.6 |  | 98.4 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES_1095904_CP825LCD_11082012052430_2563748
2118197 | CyberPower Systems, Inc. | CyberPower | CP685AVR-G, CP685AVR, CP685AVRLCD, CP685AVRLCD-G | CP685AVR-G, CP685AVR, CP685AVRLCD, CP685AVRLCD-G |  | Ac-output UPS | Static | CP685AVR-G | 390 | 685 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 89 | 165 | 279 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.4 |  | 97.6 |  | 98.4 |  | 98.8 |  | 98.7 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 10 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-09 | 2012-10-29 | United States | ES_1095904_CP685AVR-G,CP685AVR,CP685AVRLCD,CP685AVRLCD-G11052012025551_2563750
2118199 | CyberPower Systems, Inc. | CyberPower | CP825AVRLCD, CP825AVRLCD-G | CP825AVR-G, CP825AVRLCD, CP825AVRLCD-G |  | Ac-output UPS | Static | CP825AVRLCD | 450 | 825 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 89 | 165 | 279 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.8 |  | 97.6 |  | 98.4 |  | 99.1 |  | 98.7 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-09 | 2012-10-29 | United States | ES_1095904_CP825AVR-G, CP825AVRLCD, CP825AVRLCD-G11052012025551_2563750
2118319 | CyberPower Systems, Inc. | CyberPower | CP850AVRLCD | CP850AVRLCD |  | Ac-output UPS | Static | CP850AVRLCD | 510 | 850 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 222 | 108 | 267 | 9 | 5 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4 |  | 96.6 |  | 97.9 |  | 98.3 |  | 98.4 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 1 | 7 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP850AVRLCD_11092012040246_2563751
2118320 | CyberPower Systems, Inc. | CyberPower | CP900AVR, CP900D | CP900AVR, CP900D |  | Ac-output UPS | Static | CP900AVR | 560 | 900 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4 |  | 97 |  | 98.2 |  | 98.4 |  | 98.5 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 12 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP900AVR, CP900D_11092012040246_2563751
2118321 | CyberPower Systems, Inc. | CyberPower | CP1200AVR, CP1200D | CP1200AVR, CP1200D |  | Ac-output UPS | Static | CP1200AVR | 720 | 1200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.6 |  | 97.2 |  | 98.4 |  | 98.5 |  | 98.5 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 12 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP1200AVR, CP1200D_11092012040246_2563751
2118322 | CyberPower Systems, Inc. | CyberPower | CP1350AVRLCD | CP1350AVRLCD |  | Ac-output UPS | Static | CP1350AVRLCD | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 4 |  | 97.9 |  | 98.5 |  | 98.4 |  | 98.3 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 9 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP1350AVRLCD_11092012040246_2563751
2118323 | CyberPower Systems, Inc. | CyberPower | CP1500AVRT, CP1500AVR , CP1500D | CP1500AVRT, CP1500AVR , CP1500D |  | Ac-output UPS | Static | CP1500AVRT | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 4.4 |  | 97.6 |  | 98.3 |  | 98.3 |  | 98.2 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP1500AVRT, CP1500AVR , CP1500D_11092012040246_2563751
2118324 | CyberPower Systems, Inc. | CyberPower | CP1500AVRLCD, CP1500C | CP1500AVRLCD, CP1500C |  | Ac-output UPS | Static | CP1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 4.8 |  | 97.3 |  | 98.2 |  | 98.2 |  | 98.2 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP1500AVRLCD, CP1500C_11092012040246_2563751
2122338 | CyberPower Systems, Inc. | CyberPower | OR2200LCDRTXL2U | OR2200LCDRTXL2U |  | Ac-output UPS | Static | OR2200LCDRTXL2U | 1650 | 2190 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 47-63 | 125-125 | 47-63 | No |  | 89 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 13.6 |  | 96.8 |  | 97.3 |  | 97.3 |  | 97.5 |  | 97.2 | [8 empty] | 0.99 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 6 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR2200LCDRTXL2U_11122012024902_2563757
2122342 | CyberPower Systems, Inc. | CyberPower | PR750LCDRM1U | PR750LCDRM1U |  | Ac-output UPS | Static | PR750LCDRM1U | 560 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 120-120 | 47-63 | Yes |  | 44 | 495 | 438 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.4 |  | 95.2 |  | 97.3 |  | 97.6 |  | 99.8 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 7 | 23 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR750LCDRM1U11122012032318_2563741
2122343 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRM1U | PR1000LCDRM1U |  | Ac-output UPS | Static | PR1000LCDRM1U | 750 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 120-120 | 47-63 | Yes |  | 44 | 495 | 438 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.4 |  | 96.2 |  | 97.6 |  | 97.4 |  | 97.5 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1000LCDRM1U11122012032318_2563741
2122346 | CyberPower Systems, Inc. | CyberPower | PR2200LCDRT2U | PR2200LCDRT2U |  | Ac-output UPS | Static | PR2200LCDRT2U | 1980 | 2150 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 400 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 10.24 |  | 97 |  | 98.1 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 6 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR2200LCDRT2U11122012032318_2563741
2122348 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRTXL2U | PR1000LCDRTXL2U |  | Ac-output UPS | Static | PR1000LCDRTXL2U | 900 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 400 | 438 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 7.6 |  | 95.9 |  | 96.3 |  | 97 |  | 97.1 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 11 | 32 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1000LCDRTXL2U11122012032318_2563741
2122349 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRTXL2Ua | PR1000LCDRTXL2Ua |  | Ac-output UPS | Static | PR1000LCDRTXL2Ua | 1000 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 7.2 |  | 96.4 |  | 96.6 |  | 97.1 |  | 97.3 |  | 97 | [8 empty] | 1 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 18 | 39 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1000LCDRTXL2Ua11122012032318_2563741
2122350 | CyberPower Systems, Inc. | CyberPower | PR1500LCDRTXL2U | PR1500LCDRTXL2U |  | Ac-output UPS | Static | PR1500LCDRTXL2U | 1500 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 11.2 |  | 95.6 |  | 97.3 |  | 97.8 |  | 97.9 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 9 | 24 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1500LCDRTXL2U11122012032318_2563741
2122351 | CyberPower Systems, Inc. | CyberPower | PR2200LCDRTXL2U | PR2200LCDRTXL2U |  | Ac-output UPS | Static | PR2200LCDRTXL2U | 2150 | 2150 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-80 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 11.2 |  | 96.7 |  | 97.8 |  | 97.9 |  | 97.8 |  | 97.9 | [8 empty] | 1 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR2200LCDRTXL2U11122012032318_2563741
2122353 | CyberPower Systems, Inc. | CyberPower | PR5000LCDRTXL5U | PR5000LCDRTXL5U |  | Ac-output UPS | Static | PR5000LCDRTXL5U | 4000 | 5000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 131-268 | 47-63 | 193-257 | 47-63 | Yes |  | 222 | 616 | 432 | 5 | 5 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 240 | 60 | 240 | 60 | 10.8 |  | 98.4 |  | 98.4 |  | 98.7 |  | 98.8 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 12 | 31 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR5000LCDRTXL5U11122012032318_2563741
2131991 | CyberPower Systems, Inc. | CyberPower | OR1500LCDRTXL2U | OR1500LCDRTXL2U |  | Ac-output UPS | Static | OR1500LCDRTXL2U | 1125 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 47-63 | 120-120 | 47-63 | No |  | 89 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 13.6 |  | 95.1 |  | 97 |  | 97.5 |  | 96.7 |  | 97.1 | [8 empty] | 1 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 7 | 19 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR1500LCDRTXL2U11192012112543_9999999
2131992 | CyberPower Systems, Inc. | CyberPower | OR500LCDRM1U | OR500LCDRM1U |  | Ac-output UPS | Static | OR500LCDRM1U | 300 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 44 | 235 | 438 | 6 | 4 | 2 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.8 |  | 95.4 |  | 98.4 |  | 98.4 |  | 98.4 |  | 98.3 | [8 empty] | 0.98 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 12 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR500LCDRM1U11192012112543_9999999
2131993 | CyberPower Systems, Inc. | CyberPower | OR700LCDRM1U | OR700LCDRM1U |  | Ac-output UPS | Static | OR700LCDRM1U | 400 | 700 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 44 | 235 | 438 | 6 | 4 | 2 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.2 |  | 96.9 |  | 98.5 |  | 98.8 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR700LCDRM1U11192012112543_9999999
2131994 | CyberPower Systems, Inc. | CyberPower | OR1000LCDRM1U | OR1000LCDRM1U |  | Ac-output UPS | Static | OR1000LCDRM1U | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 44 | 400 | 438 | 6 | 4 | 2 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.8 |  | 95.2 |  | 97.7 |  | 97.7 |  | 98.7 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR1000LCDRM1U11192012112543_9999999
2131995 | CyberPower Systems, Inc. | CyberPower | OR1500LCDRM1U | OR1500LCDRM1U |  | Ac-output UPS | Static | OR1500LCDRM1U | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 44 | 400 | 438 | 6 | 4 | 2 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 5.2 |  | 97.7 |  | 98.5 |  | 98.5 |  | 98.3 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-28 | 2012-10-23 | United States | ES_1095904_OR1500LCDRM1U11192012112543_9999999
2169628 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2U | OL1000RTXL2U |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.94 | 21 | 85.8 | 89.1 | 89.7 | 93.3 | 90 | 93.8 | 90 | 94.2 | 89.9 | 92.9 | [7 empty] | 0.99 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 6 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL1000RTXL2U_11192012111319_2578762
2169629 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2U | OL1500RTXL2U |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.58 | 32.04 | 86.3 | 90.8 | 89.8 | 94.6 | 90 | 94.9 | 89.7 | 95.2 | 89.9 | 94.1 | [7 empty] | 0.94 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 3 | 9 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL1500RTXL2U_11192012111319_2578762
2169630 | CyberPower Systems, Inc. | CyberPower | OL6KRT3UPM | OL6KRT3UPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KRT3UPM_11192012111252_2578761
2169631 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UPM | OL6KERT3UPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KERT3UPM_11192012111252_2578761
2169632 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UDPM | OL6KERT3UDPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KERT3UDPM_11192012111252_2578761
2169633 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UPM | OL8KRT3UPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UPM_11192012111252_2578761
2169634 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UPM | OL8KERT3UPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UPM_11192012111252_2578761
2169635 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UDPM | OL8KERT3UDPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UDPM_11192012111252_2578761
2169636 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UPM | OL10KRT3UPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 203.2 | 89.8 | 91.1 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 95.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_11192012111252_2578761
2169637 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UPM | OL10KERT3UPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UPM_11192012111252_2578761
2169638 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UDPM | OL10KERT3UDPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UDPM_11192012111252_2578761
2176517 | CyberPower Systems, Inc. | CyberPower | CP350COM | CP350COM |  | Ac-output UPS | Static | CP350SLG | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.92 |  | 94.1 |  | 96.6 |  | 97.5 |  | 97.6 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ CP350COM_04022013005946_4386829
2176518 | CyberPower Systems, Inc. | CyberPower | CP350SLG | CP350SLG |  | Ac-output UPS | Static | CP350SLG | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.92 |  | 94.1 |  | 96.6 |  | 97.5 |  | 97.6 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ CP350SLG_04022013005930_4370749
2176519 | CyberPower Systems, Inc. | CyberPower | CP425G3 | CP425G3 |  | Ac-output UPS | Static | CP350SLG | 390 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.38 |  | 96.4 |  | 98.9 |  | 98.9 |  | 97.4 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | N/A | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ CP425G3_04022013010049_4449076
2176520 | CyberPower Systems, Inc. | CyberPower | CST350NET | CST350NET |  | Ac-output UPS | Static | CP350SLG | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.92 |  | 94.1 |  | 96.6 |  | 97.5 |  | 97.6 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ CST350NET_04022013010030_4430885
2176521 | CyberPower Systems, Inc. | CyberPower | HN350COM | HN350COM |  | Ac-output UPS | Static | CP350SLG | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 81 | 180 | 109 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.92 |  | 94.1 |  | 96.6 |  | 97.5 |  | 97.6 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ HN350COM_04022013010006_4406673
2176567 | CyberPower Systems, Inc. | CyberPower | EC650LCD | EC650LCD |  | Ac-output UPS | Static | EC650LCD | 390 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 78 | 269 | 149 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.38 |  | 96.4 |  | 98.9 |  | 98.9 |  | 97.4 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | N/A | 2013-03-28 | 2013-04-01 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ EC650LCD_04022013010106_4466686
2177028 | CyberPower Systems, Inc. | CyberPower | EC550G | EC550G |  | Ac-output UPS | Static | EC550G | 330 | 550 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 269 | 149 | 78 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.22 |  | 95.8 |  | 97.6 |  | 98.1 |  | 98.2 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-05-01 | 2013-04-02 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ EC550G_04092013051324_4404000
2177029 | CyberPower Systems, Inc. | CyberPower | EC350G | EC350G |  | Ac-output UPS | Static | EC350G | 255 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 269 | 149 | 78 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.34 |  | 94.4 |  | 97.1 |  | 97.9 |  | 98 |  | 97.1 | [8 empty] | 0.99 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-05-01 | 2013-04-02 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ EC350G_04092013051242_4362894
2177030 | CyberPower Systems, Inc. | CyberPower | EC750G | EC750G |  | Ac-output UPS | Static | EC750G | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 309 | 177 | 78 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.4 |  | 96.6 |  | 97.9 |  | 98.2 |  | 98.3 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-05-01 | 2013-04-02 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ EC750G_04092013051341_4421292
2177031 | CyberPower Systems, Inc. | CyberPower | EC850LCD | EC850LCD |  | Ac-output UPS | Static | EC850LCD | 510 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 309 | 177 | 78 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.55 |  | 97 |  | 98 |  | 98.3 |  | 98.2 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-05-01 | 2013-04-02 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ EC850LCD_04092013051420_4460908
2177032 | CyberPower Systems, Inc. | CyberPower | SX750 | SX750 |  | Ac-output UPS | Static | EC750G | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 309 | 177 | 78 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.4 |  | 96.6 |  | 97.9 |  | 98.2 |  | 98.3 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf |  | None | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-CP350SLG.pdf | 2013-05-01 | 2013-04-02 | United States, Canada | ES_1105798_CYBER POWER SYSTEMS INC (77215) ¦ SX750_04092013051402_4442165
2178818 | CyberPower Systems, Inc. | CyberPower | LX1000G | LX1000G |  | Ac-output UPS | Static | CP1000AVRLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 60-61 | No |  | 225 | 110 | 260 | 9 | 5 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.94 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.7 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 1 | 6 | 1 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2009-01-15 | 2012-10-09 | United States | ES__0425201LX1000G04252013051800_2617594
2178819 | CyberPower Systems, Inc. | CyberPower | SE425G | SE425G |  | Ac-output UPS | Static | CP425HG | 255 | 425 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 93.4 |  | 96.7 |  | 97.8 |  | 98 |  | 96.7 | [8 empty] | 1 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 7 | 2 | N/A |  | Serial Port,USB Port | Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201SE425G04252013053748_2615861
2178820 | CyberPower Systems, Inc. | CyberPower | SX500G | SX500G |  | Ac-output UPS | Static | CP500HG | 300 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 95 |  | 97.2 |  | 98 |  | 98.3 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201SX500G04252013053748_2615861
2178821 | CyberPower Systems, Inc. | CyberPower | SX550G | SX550G |  | Ac-output UPS | Static | CP550HG | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 100-140 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.4 |  | 95 |  | 97.7 |  | 98.3 |  | 98.5 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201SX550G04252013053748_2615861
2178822 | CyberPower Systems, Inc. | CyberPower | CP550SLGTAA | CP550SLGTAA |  | Ac-output UPS | Static | CP550HG | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 120-120 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.4 |  | 95 |  | 97.7 |  | 98.3 |  | 98.5 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201CP550SLGTAA04252013053748_2615861
2178823 | CyberPower Systems, Inc. | CyberPower | SX625G | SX625G |  | Ac-output UPS | Static | CP625HG | 375 | 625 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 120-120 | 47-63 | No |  | 83 | 159 | 248 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.4 |  | 95.6 |  | 97.5 |  | 98.3 |  | 98.5 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 8 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201SX625G04252013053748_2615861
2178824 | CyberPower Systems, Inc. | CyberPower | CP750LCDTAA | CP750LCDTAA |  | Ac-output UPS | Static | CP750LCD | 420 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 96-140 | 47-63 | 120-120 | 47-63 | No |  | 83 | 165 | 278 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.2 |  | 96.7 |  | 97.8 |  | 97.4 |  | 98.3 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 10 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-22 | 2012-10-26 | United States | ES__0425201CP750LCDTAA04252013053748_2615861
2178827 | CyberPower Systems, Inc. | CyberPower | CP1000PFCLCDTAA | CP1000PFCLCDTAA |  | Ac-output UPS | Static | CP1000PFCLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 231 | 99 | 264 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 96.5 |  | 98.1 |  | 98.4 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 9 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES__0425201CP1000PFCLCDTAA04252013055820_2617598
2178828 | CyberPower Systems, Inc. | CyberPower | CP1500PFCLCDTAA | CP1500PFCLCDTAA |  | Ac-output UPS | Static | CP1500PFCLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.8 |  | 98.5 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES__0425201CP1500PFCLCDTAA04252013055820_2617598
2178829 | CyberPower Systems, Inc. | CyberPower | PR750LCDTAA | PR750LCDTAA |  | Ac-output UPS | Static | PR750LCD | 525 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 75-154 | 47-63 | 120-120 | 47-63 | No |  | 162 | 349 | 138 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.4 |  | 97.6 |  | 97.2 |  | 97.8 |  | 98 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 15 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-05-14 | 2012-06-15 | United States | ES__0425201 PR750LCDTAA04252013061625_2617599
2179451 | CyberPower Systems, Inc. | CyberPower | CP1350AVRLCD | CP1350AVRLCD |  | Ac-output UPS | Static | CP1350AVRLCD | 810 | 1325 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 4 |  | 97.9 |  | 98.5 |  | 98.4 |  | 98.3 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 9 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_CP1350AVRLCD_05082013111629_2617597
2179456 | CyberPower Systems, Inc. | CyberPower | LX1500G | LX1500G |  | Ac-output UPS | Static | CP1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 120-120 | 57-63 | No |  | 248 | 102 | 337 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 4.8 |  | 97.3 |  | 98.2 |  | 98.2 |  | 98.2 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other,SNMP (v1, 2 or 3),HTTP | (TCP/IP, UDP) | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-20 | 2012-10-22 | United States | ES_1095904_LX1500G_05082013111626_2617597
2181611 | CyberPower Systems, Inc. | CyberPower | PR2200LCDRT2UTAA | PR2200LCDRT2UTAA |  | Ac-output UPS | Static | PR2200LCDRT2U | 1980 | 2150 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 400 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 10.24 |  | 97 |  | 98.1 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 6 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR2200LCDRT2UTAA05232013064827_2617595
2181614 | CyberPower Systems, Inc. | CyberPower | PR1500LCDRTXL2UTAA | PR1500LCDRTXL2UTAA |  | Ac-output UPS | Static | PR1500LCDRTXL2U | 1500 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 11.2 |  | 95.6 |  | 97.3 |  | 97.8 |  | 97.9 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 9 | 24 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1500LCDRTXL2UTAA05232013064833_2617595
2181616 | CyberPower Systems, Inc. | CyberPower | PR2200LCDRTXL2UTAA | PR2200LCDRTXL2UTAA |  | Ac-output UPS | Static | PR2200LCDRTXL2U | 2150 | 2150 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-80 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 11.2 |  | 96.7 |  | 97.8 |  | 97.9 |  | 97.8 |  | 97.9 | [8 empty] | 1 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR2200LCDRTXL2UTAA05232013064835_2617595
2181619 | CyberPower Systems, Inc. | CyberPower | PR5000LCDRTXL5UTAA | PR5000LCDRTXL5UTAA |  | Ac-output UPS | Static | PR5000LCDRTXL5U | 4000 | 5000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 131-268 | 47-63 | 193-257 | 47-63 | Yes |  | 222 | 616 | 432 | 5 | 5 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 240 | 60 | 240 | 60 | 10.8 |  | 98.4 |  | 98.4 |  | 98.7 |  | 98.8 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 12 | 31 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR5000LCDRTXL5UTAA05232013064838_2617595
2189284 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRT2U | PR1000LCDRT2U |  | Ac-output UPS | Static | PR1000LCDRT2U | 900 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 114-126 | 47-63 | Yes |  | 88 | 400 | 438 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 7.46 |  | 96.3 |  | 97.3 |  | 97 |  | 97 |  | 97.1 | [8 empty] | 0.99 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 9 | 23 | 2 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR1000LCDRT2U.pdf |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR1000LCDRT2U.pdf | 2012-04-11 | 2013-08-28 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR1000LCDRT2U_08302013080911_0151792
2189285 | CyberPower Systems, Inc. | CyberPower | PR1500LCDRT2U | PR1500LCDRT2U |  | Ac-output UPS | Static | PR1500LCDRT2U | 1350 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 114-126 | 47-63 | Yes |  | 88 | 400 | 438 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 7.38 |  | 96.7 |  | 97.7 |  | 96.7 |  | 96.6 |  | 97 | [8 empty] | 0.99 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 13 | 2 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR1500LCDRT2U.pdf |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR1500LCDRT2U.pdf | 2012-04-11 | 2013-08-28 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR1500LCDRT2U_08302013080929_0169869
2189286 | CyberPower Systems, Inc. | CyberPower | PR3000LCDRT2U | PR3000LCDRT2U |  | Ac-output UPS | Static | PR3000LCDRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 114-126 | 47-63 | Yes |  | 88 | 495 | 438 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 0.2 |  | 95.8 |  | 98.8 |  | 96.6 |  | 97.6 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 9 | 2 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR3000LCDRT2U.pdf |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR3000LCDRT2U.pdf | 2012-04-11 | 2013-08-28 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR3000LCDRT2U_08302013080949_0189286
2189287 | CyberPower Systems, Inc. | CyberPower | PR3000LCDRTXL2U | PR3000LCDRTXL2U |  | Ac-output UPS | Static | PR3000LCDRT2U | 3000 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 114-126 | 47-63 | Yes |  | 88 | 495 | 597 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 0.2 |  | 95.8 |  | 98.8 |  | 96.6 |  | 97.6 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.5 | 8 | 2 | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR3000LCDRTXL2U.pdf |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/spec-sheets/CyberPower-datasheet-PR3000LCDRTXL2U.pdf | 2012-04-11 | 2013-08-28 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR3000LCDRTXL2U_08302013081010_0210866
2189918 | CyberPower Systems, Inc. | CyberPower | OR1500LCDRT2U | OR1500LCDRT2U | CPS1500AVRa,CPS1500AVRa, | Ac-output UPS | Static | OR1500LCDRT2U | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 90-140 | 47-63 | 108-132 | 49-61 | Yes |  | 88 | 438 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.35 |  | 98.1 |  | 98.4 |  | 98.3 |  | 98 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 18 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-09-18 | 2013-09-06 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OR1500LCDRT2U_09092013070513_0313178
2189919 | CyberPower Systems, Inc. | CyberPower | OR2200LCDRT2U | OR2200LCDRT2U |  | Ac-output UPS | Static | OR2200LCDRT2U | 1320 | 2000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 90-140 | 47-63 | 108-132 | 49-61 | Yes |  | 88 | 438 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.5 |  | 98.7 |  | 98.9 |  | 98.8 |  | 98.6 |  | 98.8 | [8 empty] | 0.99 | [22 empty] | 98.8 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 13 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-09-18 | 2013-09-06 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OR2200LCDRT2U_09092013070537_0337276
2191866 | CyberPower Systems, Inc. | CyberPower | PR2200LCDSL | PR2200LCDSL |  | Ac-output UPS | Static | PR2200LCDSL | 1980 | 2070 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 72-157 | 57-63 | 114-126 | 59-61 | No |  | 222 | 170 | 233 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 120 | 6 |  | 98.3 |  | 98.7 |  | 98.6 |  | 98.4 |  | 98.6 | [8 empty] | 0.99 | [22 empty] | 98.6 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 0.20138888888888887 | 0.4930555555555556 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-10-23 | 2013-09-11 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR2200LCDSL_09162013094134_4494057
2191867 | CyberPower Systems, Inc. | CyberPower | PR3000LCDSL | PR3000LCDSL |  | Ac-output UPS | Static | PR3000LCDSL | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 72-157 | 57-63 | 114-126 | 59-61 | No |  | 222 | 170 | 233 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 60 | 60 | 6.64 |  | 98.6 |  | 98.7 |  | 98.6 |  | 98.1 |  | 98.5 | [8 empty] | 0.99 | [22 empty] | 98.5 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 0.1111111111111111 | 0.3263888888888889 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-10-23 | 2013-09-11 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR3000LCDSL_09162013094153_4513997
2191982 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2U | OL2200RTXL2U |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 42.7 | 42.71 | 86 | 91.6 | 89.6 | 94.9 | 89.3 | 95.8 | 89.3 | 95.5 | 89.3 | 91 | [7 empty] | 0.99 | 0.99 | [21 empty] | 89.3 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 17 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-07-01 | 2013-09-23 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OL2200RTXL2U_09262013113739_5459040
2191983 | CyberPower Systems, Inc. | CyberPower | OL2200RT JP | OL2200RT JP |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 42.7 | 42.71 | 86 | 91.6 | 89.6 | 94.9 | 89.3 | 95.8 | 89.3 | 95.5 | 89.3 | 91 | [7 empty] | 0.99 | 0.99 | [21 empty] | 89.3 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 17 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-07-01 | 2013-09-23 | United States, Japan | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OL2200RT JP_09262013113824_5504159
2191984 | CyberPower Systems, Inc. | CyberPower | OL3000RT JP | OL3000RT JP |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 59.1 | 55.67 | 85.6 | 91.6 | 89.2 | 94.8 | 89.2 | 95.6 | 89.2 | 95.2 | 88.9 | 90.7 | [7 empty] | 0.99 | 0.99 | [21 empty] | 88.9 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-07-01 | 2013-09-23 | United States, Japan | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OL3000RT JP_09262013113843_5523025
2191985 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2U | OL3000RTXL2U |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 59.1 | 55.67 | 85.6 | 91.6 | 89.2 | 94.8 | 89.2 | 95.6 | 89.2 | 95.2 | 88.9 | 90.7 | [7 empty] | 0.99 | 0.99 | [21 empty] | 88.9 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-07-01 | 2013-09-23 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ OL3000RTXL2U_09262013113758_5478227
2198379 | CyberPower Systems, Inc. | CyberPower | AVRG750U | AVRG750U |  | Ac-output UPS | Static | AVRG750U | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 108-132 | 59-61 | No |  | 90 | 180 | 311 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.82 |  | 95.8 |  | 98.9 |  | 98.1 |  | 98.2 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 22 | 8 | 3 | http://www.cyberpowersystems.com/region-selector.html |  | None | Other | HID | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/region-selector.html | 2014-01-31 | 2013-12-09 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ AVRG750U_12122013020616_3976118
2198380 | CyberPower Systems, Inc. | CyberPower | AVRG900U | AVRG900U |  | Ac-output UPS | Static | AVRG900U | 480 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 108-132 | 59-61 | No |  | 90 | 180 | 311 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.68 |  | 96.5 |  | 98 |  | 98.3 |  | 98.4 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 28.5 | 11.5 | 3 | http://www.cyberpowersystems.com/region-selector.html |  | None | Other | HID | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/region-selector.html | 2014-01-31 | 2013-12-09 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ AVRG900U_12122013020634_3994628
2204859 | CyberPower Systems, Inc. | CyberPower | BRG1350AVRLCD | BRG1350AVRLCD |  | Ac-output UPS | Static | BRG1500AVRLCD | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 108-132 | 59-61 | No |  | 28 | 100 | 355 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.67 |  | 96.3 |  | 97.6 |  | 97.6 |  | 97.5 |  | 97.6 | [8 empty] | 0.6 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-05-15 | 2014-02-20 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ BRG1350AVRLCD_02202014075404_2844532
2204860 | CyberPower Systems, Inc. | CyberPower | BRG1500AVRLCD | BRG1500AVRLCD |  | Ac-output UPS | Static | BRG1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 108-132 | 59-61 | No |  | 28 | 100 | 355 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 129 | 60 | 7.67 |  | 96.3 |  | 97.6 |  | 97.6 |  | 97.5 |  | 97.6 | [8 empty] | 0.6 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-05-15 | 2014-02-20 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ BRG1500AVRLCD_02202014075435_2875561
2204981 | CyberPower Systems, Inc. | CyberPower | OL1000RT JP | OL1000RT JP |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.94 | 21 | 85.8 | 89.1 | 89.7 | 93.3 | 90 | 93.8 | 90 | 94.2 | 89.9 | 92.9 | [7 empty] | 0.99 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 6 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Japan, Canada | ES_1095904_OL1000RT JP_02242014043251_8888888
2204982 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2UTAA | OL1000RTXL2UTAA |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.94 | 21 | 85.8 | 89.1 | 89.7 | 93.3 | 90 | 93.8 | 90 | 94.2 | 89.9 | 92.9 | [7 empty] | 0.99 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 6 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL1000RTXL2UTAA_02242014043252_8888888
2204983 | CyberPower Systems, Inc. | CyberPower | OL1500RT JP | OL1500RT JP |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.58 | 32.04 | 86.3 | 90.8 | 89.8 | 94.6 | 90 | 94.9 | 89.7 | 95.2 | 89.9 | 94.1 | [7 empty] | 0.94 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 3 | 9 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Japan, Canada | ES_1095904_OL1500RT JP_02242014043253_8888888
2204984 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2UTAA | OL1500RTXL2UTAA |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.58 | 32.04 | 86.3 | 90.8 | 89.8 | 94.6 | 90 | 94.9 | 89.7 | 95.2 | 89.9 | 94.1 | [7 empty] | 0.94 | 1 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 3 | 9 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-08-30 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL1500RTXL2UTAA_02242014043254_8888888
2205066 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UTFTAA | OL8000RT3UTFTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UTFTAA_02262014025037_8888888
2205067 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UPDUPMTAA | OL8KRT3UPDUPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UPDUPMTAA_02262014025038_8888888
2205068 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UPDUTAA | OL8000RT3UPDUTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UPDUTAA_02262014025039_8888888
2205069 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UHWTAA | OL8KRT3UHWTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UHWTAA_02262014025040_8888888
2205070 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UPDUTFTAA | OL8000RT3UPDUTFTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UPDUTFTAA_02262014025041_8888888
2205071 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3U | OL8000ERT3U |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3U_02262014025042_8888888
2205072 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UPPM | OL8KERT3UPPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UPPM_02262014025043_8888888
2205073 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UP | OL8000ERT3UP |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UP_02262014025044_8888888
2205074 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UM | OL8000ERT3UM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UM_02262014025045_8888888
2205075 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UPMTAA | OL8KERT3UPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UPMTAA_02262014025046_8888888
2205076 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UTAA | OL8000ERT3UTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UTAA_02262014025047_8888888
2205077 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UPPMTAA | OL8KERT3UPPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UPPMTAA_02262014025048_8888888
2205078 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UPTAA | OL8000ERT3UPTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UPTAA_02262014025049_8888888
2205079 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UMTAA | OL8000ERT3UMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UMTAA_02262014025050_8888888
2205080 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UD | OL8000ERT3UD |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UD_02262014025051_8888888
2205081 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UDMPM | OL8KERT3UDMPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UDMPM_02262014025052_8888888
2205082 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UDM | OL8000ERT3UDM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UDM_02262014025053_8888888
2205083 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UDPMTAA | OL8KERT3UDPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UDPMTAA_02262014025054_8888888
2205084 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UDTAA | OL8000ERT3UDTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UDTAA_02262014025055_8888888
2205085 | CyberPower Systems, Inc. | CyberPower | OL8KERT3UDMPMTAA | OL8KERT3UDMPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KERT3UDMPMTAA_02262014025056_8888888
2205086 | CyberPower Systems, Inc. | CyberPower | OL8000ERT3UDMTAA | OL8000ERT3UDMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000ERT3UDMTAA_02262014025057_8888888
2205087 | CyberPower Systems, Inc. | CyberPower | OL10000RT3U | OL10000RT3U |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014025058_8888888
2205088 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UTF | OL10000RT3UTF |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014025059_8888888
2205089 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UPDU | OL10000RT3UPDU |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020059_8888888
2205090 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UHW | OL10KRT3UHW |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020159_8888888
2205091 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UPDUTF | OL10000RT3UPDUTF |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014022259_8888888
2205092 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UPMTAA | OL10KRT3UPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020359_8888888
2205093 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UTAA | OL10000RT3UTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020459_8888888
2205094 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UTFTAA | OL10000RT3UTFTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020559_8888888
2205095 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UPDUPMTAA | OL10KRT3UPDUPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020659_8888888
2205096 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UPDUTAA | OL10000RT3UPDUTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020759_8888888
2205097 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UHWTAA | OL10KRT3UHWTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020859_8888888
2205098 | CyberPower Systems, Inc. | CyberPower | OL10000RT3UPDUTFTAA | OL10000RT3UPDUTFTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPM_02262014020959_8888888
2205099 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3U | OL10000ERT3U |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3U_02262014021059_8888888
2205100 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UPPM | OL10KERT3UPPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UPPM_02262014021159_8888888
2205101 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UP | OL10000ERT3UP |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UP_02262014021259_8888888
2205102 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UM | OL10000ERT3UM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UM_02262014021359_8888888
2205103 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UPMTAA | OL10KERT3UPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UPMTAA_02262014021459_8888888
2205104 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UTAA | OL10000ERT3UTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UTAA_02262014021559_8888888
2205105 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UPPMTAA | OL10KERT3UPPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UPPMTAA_02262014021659_8888888
2205106 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UPTAA | OL10000ERT3UPTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UPTAA_02262014021759_8888888
2205107 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UMTAA | OL10000ERT3UMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UMTAA_02262014021859_8888888
2205108 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UD | OL10000ERT3UD |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UD_02262014021959_8888888
2205109 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UDMPM | OL10KERT3UDMPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UDMPM_02262014022059_8888888
2205110 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UDM | OL10000ERT3UDM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UDM_02262014022159_8888888
2205111 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UDPMTAA | OL10KERT3UDPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UDPMTAA_02262014022259_8888888
2205112 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UDTAA | OL10000ERT3UDTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UDTAA_02262014022359_8888888
2205113 | CyberPower Systems, Inc. | CyberPower | OL10KERT3UDMPMTAA | OL10KERT3UDMPMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KERT3UDMPMTAA_02262014022459_8888888
2205114 | CyberPower Systems, Inc. | CyberPower | OL10000ERT3UDMTAA | OL10000ERT3UDMTAA |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10000ERT3UDMTAA_02262014022559_8888888
2205115 | CyberPower Systems, Inc. | CyberPower | OL6000RT3U | OL6000RT3U |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3U_02262014025000_8888888
2205116 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UTF | OL6000RT3UTF |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UTF_02262014025001_8888888
2205117 | CyberPower Systems, Inc. | CyberPower | OL6KRT3UPDUPM | OL6KRT3UPDUPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KRT3UPDUPM_02262014025002_8888888
2205118 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UPDU | OL6000RT3UPDU |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UPDU_02262014025003_8888888
2205120 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UPDUTF | OL6000RT3UPDUTF |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UPDUTF_02262014025005_8888888
2205121 | CyberPower Systems, Inc. | CyberPower | OL6KRT3UPMTAA | OL6KRT3UPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KRT3UPMTAA_02262014025006_8888888
2205122 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UTAA | OL6000RT3UTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UTAA_02262014025007_8888888
2205123 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UTFTAA, | OL6000RT3UTFTAA, |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UTFTAA, _02262014025008_8888888
2205124 | CyberPower Systems, Inc. | CyberPower | OL6KRT3UPDUPMTAA | OL6KRT3UPDUPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KRT3UPDUPMTAA_02262014025009_8888888
2205125 | CyberPower Systems, Inc. | CyberPower | OL6KRT3UHWTAA | OL6KRT3UHWTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KRT3UHWTAA_02262014025010_8888888
2205126 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UPDUTAA | OL6000RT3UPDUTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UPDUTAA_02262014025011_8888888
2205127 | CyberPower Systems, Inc. | CyberPower | OL6000RT3UPDUTFTAA | OL6000RT3UPDUTFTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000RT3UPDUTFTAA_02262014025012_8888888
2205128 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3U | OL6000ERT3U |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3U_02262014025013_8888888
2205129 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UPPM | OL6KERT3UPPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KERT3UPPM_02262014025014_8888888
2205130 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UP | OL6000ERT3UP |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6000ERT3UP_02262014025015_8888888
2205131 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UM | OL6000ERT3UM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UM_02262014025016_8888888
2205132 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UPMTAA | OL6KERT3UPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6KERT3UPMTAA_02262014025017_8888888
2205133 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UTAA | OL6000ERT3UTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UTAA_02262014025018_8888888
2205134 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UPTAA | OL6000ERT3UPTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6000ERT3UPTAA_02262014025019_8888888
2205136 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UMTAA | OL6000ERT3UMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UMTAA_02262014025021_8888888
2205137 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UD | OL6000ERT3UD |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UD_02262014025022_8888888
2205138 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UDMPM | OL6KERT3UDMPM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6KERT3UDMPM_02262014025023_8888888
2205139 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UDM | OL6000ERT3UDM |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UDM_02262014025024_8888888
2205140 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UDPMTAA | OL6KERT3UDPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KERT3UDPMTAA_02262014025025_8888888
2205141 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UDTAA | OL6000ERT3UDTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6000ERT3UDTAA_02262014025026_8888888
2205142 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UDMPMTAA | OL6KERT3UDMPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_ OL6KERT3UDMPMTAA_02262014025027_8888888
2205143 | CyberPower Systems, Inc. | CyberPower | OL6000ERT3UDMTAA | OL6000ERT3UDMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 5750 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6000ERT3UDMTAA_02262014025028_8888888
2205144 | CyberPower Systems, Inc. | CyberPower | OL8000RT3U | OL8000RT3U |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3U_02262014025029_8888888
2205145 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UTF | OL8000RT3UTF |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UTF_02262014025030_8888888
2205146 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UPDUPM | OL8KRT3UPDUPM |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UPDUPM_02262014025031_8888888
2205147 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UPDU | OL8000RT3UPDU |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UPDU_02262014025032_8888888
2205148 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UHW | OL8KRT3UHW |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UHW_02262014025033_8888888
2205149 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UPDUTF | OL8000RT3UPDUTF |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UPDUTF_02262014025034_8888888
2205150 | CyberPower Systems, Inc. | CyberPower | OL8KRT3UPMTAA | OL8KRT3UPMTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8KRT3UPMTAA_02262014025035_8888888
2205151 | CyberPower Systems, Inc. | CyberPower | OL8000RT3UTAA | OL8000RT3UTAA |  | Ac-output UPS | Static | OL8KRT3UPM | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 8 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 142.84 | 139.88 | 88.8 | 92 | 91.4 | 95.2 | 91.6 | 96.3 | 91.5 | 96.7 | 91.5 | 96.1 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 13 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL8000RT3UTAA_02262014025036_8888888
2205152 | CyberPower Systems, Inc. | CyberPower | OL10KRT3UPDUPM | OL10KRT3UPDUPM |  | Ac-output UPS | Static | OL10KRT3UPM | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 10 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 146.4 | 142.79 | 89.8 | 93.4 | 91.5 | 95.9 | 91.7 | 96.7 | 91.4 | 97.1 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL10KRT3UPDUPM_02262014044533_8888888
2205265 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRT1U | PR1000LCDRT1U |  | Ac-output UPS | Static | PR1000LCDRT1U | 800 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 80-150 | 57-63 | 114-126 | 60-60 | Yes |  | 44 | 433 | 402 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.49 |  | 94.3 |  | 96.5 |  | 97 |  | 97 |  | 96.9 | [8 empty] | 0.8 | [22 empty] | 96.9 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 2 | http://www.cyberpowersystems.com |  | Ethernet | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2014-01-14 | 2014-02-26 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR1000LCDRT1U_02272014075813_7893830
2205266 | CyberPower Systems, Inc. | CyberPower | PR500LCDRT1U | PR500LCDRT1U |  | Ac-output UPS | Static | PR500LCDRT1U | 400 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 80-150 | 57-63 | 114-126 | 60-60 | Yes |  | 44 | 433 | 243 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 9.08 |  | 95.8 |  | 97.1 |  | 96.7 |  | 97.2 |  | 97.1 | [8 empty] | 0.8 | [22 empty] | 97.1 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 12 | 2 | http://www.cyberpowersystems.com |  | Ethernet | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2014-01-14 | 2014-02-26 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR500LCDRT1U_02272014075721_7841309
2205267 | CyberPower Systems, Inc. | CyberPower | PR750LCDRT1U | PR750LCDRT1U |  | Ac-output UPS | Static | PR750LCDRT1U | 600 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 80-150 | 57-63 | 114-126 | 60-60 | Yes |  | 44 | 433 | 402 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.36 |  | 94.1 |  | 96.8 |  | 97.4 |  | 97.4 |  | 97.2 | [8 empty] | 0.8 | [22 empty] | 97.2 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 2 | http://www.cyberpowersystems.com |  | Ethernet | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2014-01-14 | 2014-02-26 | United States | ES_1105798_CYBERPOWER SYSTEMS INC (195388) ¦ PR750LCDRT1U_02272014075743_7863944
2207252 | CyberPower Systems, Inc. | CyberPower | OL6KERT3UPPMTAA | OL6KERT3UPPMTAA |  | Ac-output UPS | Static | OL6KRT3UPM | 5400 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 6 | 132 | 433 | 660 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 | 97.9 | 88.8 | 92.2 | 91.1 | 95.2 | 90.7 | 95.9 | 90.6 | 96.2 | 90.8 | 95.8 | [7 empty] | 0.99 | 1 | [21 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.3 | 15.8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-06-08 | 2013-01-18 | United States, Europe, Taiwan, Canada | ES_1095904_OL6KERT3UPPMTAA_03312014042618_8888888
2208033 | CyberPower Systems, Inc. | CyberPower | PR1000LCDRT2U | PR1000LCDRT2U |  | Ac-output UPS | Static | PR1000LCDRT2U | 900 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 400 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 6.8 |  | 95.4 |  | 97.2 |  | 97.8 |  | 96.1 |  | 97.1 | [8 empty] | 1 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 11 | 32 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1000LCDRT2U_04092014123546_8888888
2208034 | CyberPower Systems, Inc. | CyberPower | PR1500LCDRT2U | PR1500LCDRT2U |  | Ac-output UPS | Static | PR1500LCDRT2U | 1350 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 400 | 438 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 8 |  | 97.3 |  | 98.4 |  | 98.6 |  | 98.7 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 6 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR1500LCDRT2U_04092014123547_8888888
2208035 | CyberPower Systems, Inc. | CyberPower | PR3000LCDRT2U | PR3000LCDRT2U |  | Ac-output UPS | Static | PR3000LCDRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-150 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 438 | 9 | 9 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 10 |  | 98.3 |  | 98.8 |  | 98.5 |  | 98.3 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR3000LCDRT2U_04092014123548_8888888
2208036 | CyberPower Systems, Inc. | CyberPower | PR3000LCDRTXL2U | PR3000LCDRTXL2U |  | Ac-output UPS | Static | PR3000LCDRTXL2U | 3000 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Data Center | 80-80 | 47-63 | 125-125 | 47-63 | Yes |  | 88 | 495 | 597 | 9 | 9 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 13.2 |  | 97.9 |  | 98.5 |  | 98 |  | 98 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | http://www.cpsww.com/ | N/A | 2012-04-11 | 2012-11-01 | United States | ES_1095904_PR3000LCDRTXL2U_04092014123549_8888888
2211867 | CyberPower Systems, Inc. | CyberPower | BRG1000AVRLCD | BRG1000AVRLCD |  | Ac-output UPS | Static | BRG1000AVRLCD | 600 | 1000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 246 | 100 | 260 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 0.75 | 8.85 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-07-16 | 2014-05-27 | United States | ES_1095904_BRG1000AVRLCD_05282014065217_9937438
2211868 | CyberPower Systems, Inc. | CyberPower | BRG850AVRLCD | BRG850AVRLCD |  | Ac-output UPS | Static | BRG1000AVRLCD | 510 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 246 | 100 | 260 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 0.5 | 4.7 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-07-16 | 2014-05-27 | United States | ES_1095904_BRG850AVRLCD_05282014065158_9918824
2211876 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2UTAA | OL2200RTXL2UTAA |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 42.7 | 42.71 | 86 | 91.6 | 89.6 | 94.9 | 89.3 | 95.8 | 89.3 | 95.5 | 89.3 | 91 | [7 empty] | 0.99 | 0.99 | [21 empty] | 89.3 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 17 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-12-31 | 2014-05-27 | United States | ES_1095904_OL2200RTXL2UTAA_05282014082507_5507942
2211877 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UTAA | OL3000RTXL2UTAA |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 98-127 | 50-60 | Yes |  | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 59.1 | 55.67 | 85.6 | 91.6 | 89.2 | 94.8 | 89.2 | 95.6 | 89.2 | 95.2 | 88.9 | 90.7 | [7 empty] | 0.99 | 0.99 | [21 empty] | 88.9 | No | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | http://www.cyberpowersystems.com |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com | 2013-12-31 | 2014-05-27 | United States | ES_1095904_OL3000RTXL2UTAA_05282014084720_6840046
2212772 | CyberPower Systems, Inc. | CyberPower | CST1300ALU | CST1300ALU |  | Ac-output UPS | Static | CST1500ALU | 810 | 1300 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-06-09 | United States | ES_1095904_CST1300ALU_06092014091351_5231987
2212773 | CyberPower Systems, Inc. | CyberPower | CST1500ALU | CST1500ALU | CST150XLU,CST150XLU, | Ac-output UPS | Static | CST1500ALU | 900 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-06-09 | United States | ES_1095904_CST1500ALU_06092014091419_5259699
2219809 | CyberPower Systems, Inc. | CyberPower | CST1400S | CST1400S |  | Ac-output UPS | Static | CP1500PFCLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 102-138 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.8 |  | 98.5 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_CST1400S_09182014062036_2760612
2219811 | CyberPower Systems, Inc. | CyberPower | GX1325U | GX1325U |  | Ac-output UPS | Static | CP1350PFCLCD | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 102-138 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.5 |  | 98.5 |  | 98.7 |  | 98.8 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 9 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_GX1325U_09182014062036_2760612
2226187 | CyberPower Systems, Inc. | CyberPower | LX1100G | LX1100G |  | Ac-output UPS | Static | CST1500ALU | 660 | 1100 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-11-07 | United States | ES_1095904_LX1100G_12012014085205_3925689
2226188 | CyberPower Systems, Inc. | CyberPower | CST135XLU | CST135XLU |  | Ac-output UPS | Static | CST1500ALU | 810 | 1350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-11-07 | United States | ES_1095904_CST135XLU_12012014085040_3840264
2226189 | CyberPower Systems, Inc. | CyberPower | LX1325GU | LX1325GU |  | Ac-output UPS | Static | CST1500ALU | 810 | 1325 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-11-07 | United States | ES_1095904_LX1325GU_12012014085136_3896635
2226190 | CyberPower Systems, Inc. | CyberPower | LX1500GU | LX1500GU |  | Ac-output UPS | Static | CST1500ALU | 900 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 248 | 100 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.63 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-06-27 | 2014-11-07 | United States | ES_1095904_LX1500GU_12012014085111_3871267
2229524 | CyberPower Systems, Inc. | CyberPower | CP425HGa | CP425HGa |  | Ac-output UPS | Static | SE450G | 255 | 425 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 84 | 147 | 249 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.73 |  | 94.3 |  | 96.8 |  | 97.5 |  | 97.8 |  | 96.8 | [8 empty] | 0.99 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-23 | 2014-12-12 | United States | ES_1095904_CP425HGa_12172014070151_9711031
2229525 | CyberPower Systems, Inc. | CyberPower | SE450G | SE450G |  | Ac-output UPS | Static | SE450G | 260 | 425 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 84 | 147 | 249 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.73 |  | 94.3 |  | 96.8 |  | 97.5 |  | 97.8 |  | 96.8 | [8 empty] | 0.99 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-23 | 2014-12-12 | United States | ES_1095904_SE450G_12172014070125_9685753
2229572 | CyberPower Systems, Inc. | CyberPower | CP625HGa | CP625HGa | CST625G,CST625G,; SX625G,SX625G,; SX650G,SX650G,; SYC-625BB,SYC-625BB, | Ac-output UPS | Static | SX625G | 375 | 625 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 249 | 147 | 84 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.85 |  | 95.9 |  | 97.5 |  | 98 |  | 98.1 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 8 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2014-12-30 | 2014-12-17 | United States | ES_1095904_CP625HGa_12182014033702_3822532
2232859 | CyberPower Systems, Inc. | CyberPower | LE1000DG | LE1000DG |  | Ac-output UPS | Static | LE1000DG | 530 | 1000 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.2 |  | 95.9 |  | 97.6 |  | 98 |  | 98 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 10 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-01-30 | 2015-02-04 | United States | ES_1095904_LE1000DG-1_02092015082812_0492390
2232860 | CyberPower Systems, Inc. | CyberPower | AVRG750LCD | AVRG750LCD |  | Ac-output UPS | Static | AVRG750LCD | 450 | 750 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.6 |  | 95.9 |  | 97.6 |  | 98.2 |  | 98.2 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-03-01 | 2015-02-04 | United States | ES_1095904_AVRG750LCD_02092015082923_0563206
2232862 | CyberPower Systems, Inc. | CyberPower | LE850G | LE850G |  | Ac-output UPS | Static | LE850G | 460 | 825 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.5 |  | 96 |  | 97.6 |  | 98 |  | 98.2 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-01-30 | 2015-02-04 | United States | ES_1095904_LE850G_02092015084323_1403997
2232863 | CyberPower Systems, Inc. | CyberPower | AVRG750UM | AVRG750UM |  | Ac-output UPS | Static | AVRG750LCD | 450 | 750 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.6 |  | 95.9 |  | 97.6 |  | 98.2 |  | 98.2 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 7 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-28 | 2015-02-04 | United States | ES_1095904_AVRG750UM-2_02092015084232_1352120
2232865 | CyberPower Systems, Inc. | CyberPower | AVRG900LCD | AVRG900LCD |  | Ac-output UPS | Static | AVRG900LCD | 480 | 900 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.8 |  | 95.9 |  | 97.6 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 10 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-03-01 | 2015-02-04 | United States | ES_1095904_AVRG900LCD_02092015082625_0385000
2232873 | CyberPower Systems, Inc. | CyberPower | AVRG900UM | AVRG900UM |  | Ac-output UPS | Static | AVRG900LCD | 480 | 900 |  |  |  | Other | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 180 | 311 | 90 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.8 |  | 95.9 |  | 97.6 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 10 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | No |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-28 | 2015-02-04 | United States | ES_1095904_AVRG900UM_02092015082731_0451116
2235724 | CyberPower Systems, Inc. | CyberPower | OR1000PFCLCD | OR1000PFCLCD |  | Ac-output UPS | Static | OR1500PFCLCD | 700 | 1000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 138 | 350 | 166 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.77 |  | 97.1 |  | 97.8 |  | 97.8 |  | 97.5 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 15 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-28 | 2014-12-22 | United States | ES_1095904_OR1000PFCLCD_04032015041554_4554072
2235725 | CyberPower Systems, Inc. | CyberPower | OR1500PFCLCD | OR1500PFCLCD |  | Ac-output UPS | Static | OR1500PFCLCD | 1050 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 138 | 350 | 166 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.77 |  | 97.1 |  | 97.8 |  | 97.8 |  | 97.5 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 11 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-28 | 2014-12-22 | United States | ES_1095904_OR1500PFCLCD_04032015020404_6644063
2235726 | CyberPower Systems, Inc. | CyberPower | OR750PFCLCD | OR750PFCLCD |  | Ac-output UPS | Static | OR750PFCLCD | 525 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 138 | 350 | 166 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.18 |  | 95.2 |  | 97.3 |  | 97.8 |  | 98 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 13 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | Other |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2015-02-28 | 2014-12-22 | United States | ES_1095904_OR750PFCLCD_04032015041703_4623011
2236129 | CyberPower Systems, Inc. | CyberPower | OL3000XL | OL3000XL | OL3000XL JP,OL3000XL JP,; OL3000XL,OL3000XL,; OL3000XLTAA,OL3000XLTAA, | Ac-output UPS | Static | OL3000XL | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 125-125 | 50-60 | 125-125 | 50-60 | No |  | 336 | 212 | 414 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 62.46 | 62.47 | 87.1 | 86.6 | 90 | 89.8 | 90.2 | 90.2 | 89.3 | 89.8 | 89.8 | 89.9 | [7 empty] | 0.99 | 0.99 | [21 empty] | 89.9 | OL3000XL | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2015-05-01 | 2015-04-10 | United States, Canada | ES_1095904_OL3000XL_04102015094309_8989777
2236184 | CyberPower Systems, Inc. | CyberPower | OL2200XL | OL2200XL | OL2200XL JP,OL2200XL JP,; OL2200XL,OL2200XL,; OL2200XLTAA,OL2200XLTAA, | Ac-output UPS | Static | OL2200XL | 1800 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 125-125 | 50-60 | 125-125 | 50-60 | No |  | 414 | 313 | 336 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 57.58 | 55.24 | 84.2 | 84.4 | 88.5 | 95.3 | 89.9 | 95 | 90.1 | 95.4 | 88.6 | 90.3 | [7 empty] | 0.99 | 0.99 | [21 empty] | 90.3 | OL2200XL | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2015-05-01 | 2015-04-10 | United States, Canada | ES_1095904_OL2200XL_04102015090630_6790593
2237325 | CyberPower Systems, Inc. | CyberPower | OL1500XL | OL1500XL | OL1500XL JP,OL1500XL JP,; OL1500XL,OL1500XL,; OL1500XLTAA,OL1500XLTAA, | Ac-output UPS | Static | OL1500XL | 1350 | 1500 |  |  |  | Multi-Mode Line Interactive | ac - Other | Consumer | 125-125 | 50-60 | 125-125 | 50-60 | No |  | 232 | 167 | 397 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 26.74 | 26.06 | 88.7 | 92.5 | 91.6 | 95.4 | 91.7 | 95.7 | 91.6 | 96.2 | 88.6 | 92.5 | [7 empty] | 0.99 | 0.99 | [21 empty] | 92.5 | OL1500XL | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2015-05-01 | 2015-04-15 | United States, Canada | ES_1095904_OL1500XL_04152015090733_8853711
2237799 | CyberPower Systems, Inc. | CyberPower | OL1000XL | OL1000XL | OL1000XL JP,OL1000XL JP,; OL1000XL,OL1000XL,; OL1000XLTAA,OL1000XLTAA, | Ac-output UPS | Static | OL1000XL | 900 | 1000 |  |  |  | Multi-Mode Line Interactive | ac - Other | Consumer | 125-125 | 50-60 | 125-125 | 50-60 | No |  | 232 | 167 | 397 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 125 | 60 | 125 | 60 | 26.51 | 26.33 | 86.3 | 89.1 | 90.7 | 93.5 | 91.6 | 94.6 | 92 | 95.1 | 88.2 | 91.9 | [7 empty] | 0.99 | 0.99 | [21 empty] | 91.9 | OL1000XL | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2015-05-01 | 2015-04-21 | United States, Canada | ES_1095904_OL1000XL_04212015095031_9831789
2250303 | CyberPower Systems, Inc. | CyberPower | PR3000ELCDRT2U | PR3000ELCDRT2U |  | Ac-output UPS | Static | PR3000ELCDRT2U | 2700 | 3000 | None |  |  | Other | ac - Other | Consumer | 230-230 | 50-60 | 230-230 | 50-60 | No |  | 433 | 88 | 480 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Dependent | 230 | 50 | 230 | 50 | 10.46 |  | 98.2 |  | 98.6 |  | 98.1 |  | 97.9 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | PR3000ELCDRT2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2015-10-01 | 2015-10-15 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR3000ELCDRT2U_10162015064858_8138765
2250304 | CyberPower Systems, Inc. | CyberPower | PR2200ELCDRT2U | PR2200ELCDRT2U |  | Ac-output UPS | Static | PR2200ELCDRT2U | 1980 | 2200 | None |  |  | Other | ac - Other | Consumer | 230-230 | 50-60 | 230-230 | 50-60 | No |  | 433 | 88 | 388 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Dependent | 230 | 50 | 230 | 50 | 10.41 |  | 97.9 |  | 98.5 |  | 98.2 |  | 98.2 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | PR2200ELCDRT2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2015-10-01 | 2015-10-15 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR2200ELCDRT2U_10162015064922_8162934
2250306 | CyberPower Systems, Inc. | CyberPower | PR1500ELCDRT2U | PR1500ELCDRT2U |  | Ac-output UPS | Static | PR1500ELCDRT2U | 1350 | 1500 | None |  |  | Other | ac - Other | Consumer | 230-230 | 50-60 | 230-230 | 50-60 | No |  | 433 | 88 | 388 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Dependent | 230 | 50 | 230 | 50 | 10.1 |  | 97.1 |  | 98.2 |  | 97.9 |  | 98.1 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | PR1500ELCDRT2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2015-10-01 | 2015-10-15 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR1500ELCDRT2U_10162015064951_8191787
2250307 | CyberPower Systems, Inc. | CyberPower | PR1000ELCDRT2U | PR1000ELCDRT2U |  | Ac-output UPS | Static | PR1000ELCDRT2U | 900 | 1000 | None |  |  | Other | ac - Other | Consumer | 230-230 | 50-60 | 230-230 | 50-60 | No |  | 433 | 88 | 388 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Dependent | 230 | 50 | 230 | 50 | 10.08 |  | 95.7 |  | 95.7 |  | 97.5 |  | 98.1 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | PR1000ELCDRT2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2015-10-01 | 2015-10-15 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR1000ELCDRT2U_10162015065022_8222886
2263041 | CyberPower Systems, Inc. | CyberPower | PR5000LCDRTXL5U | PR5000LCDRTXL5U | PR5000LCDRTXL5UTAA,PR5000LCDRTXL5UTAA, | Ac-output UPS | Static | PR5000LCDRTXL5U | 4500 | 5000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 433 | 220 | 645 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 50 | 230 | 50 | 5.38 |  | 98.8 |  | 98.7 |  | 98.5 |  | 98.3 |  | 98.5 | [8 empty] | 0.99 | [22 empty] | 98.5 | PR5000LCDRTXL5U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2016-04-01 | 2016-03-23 | United States, Europe, Canada | ES_1095904_PR5000LCDRTXL5U_03242016031924_9564211
2263287 | CyberPower Systems, Inc. | CyberPower | PR1500LCD | PR1500LCD |  | Ac-output UPS | Static | PR1500LCD | 1500 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 222 | 170 | 433 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.58 |  | 97.7 |  | 97.8 |  | 97.4 |  | 96.9 |  | 97.4 | [8 empty] | 0.99 | [22 empty] | 97.4 | PR1500LCD | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2016-03-30 | 2016-03-25 | United States, Canada | ES_1095904_PR1500LCD_03252016071437_0077644
2263288 | CyberPower Systems, Inc. | CyberPower | PR1000LCD | PR1000LCD |  | Ac-output UPS | Static | PR1000LCD | 1000 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 222 | 170 | 433 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.03 |  | 97.2 |  | 98.1 |  | 98.2 |  | 98 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | PR1000LCD | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2016-03-30 | 2016-03-25 | United States, Canada | ES_1095904_PR1000LCD_03252016071501_0101618
2263748 | CyberPower Systems, Inc. | CyberPower | RT650 | RT650 | RT500,RT500,; RT500TAA,RT500TAA,; RT650TAA,RT650TAA, | Ac-output UPS | Static | RT650 | 400 | 650 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 92 | 165 | 279 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.56 |  | 94.5 |  | 97.5 |  | 98 |  | 98.4 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | RT650 | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 5 | N/A |  | None | None |  | Yes |  | N/A | N/A | 2016-04-30 | 2016-03-29 | United States, Canada | ES_1095904_RT650_04072016054138_7699000
2263986 | CyberPower Systems, Inc. | CyberPower | CP1350AVRLCDa | CP1350AVRLCDa |  | Ac-output UPS | Static | CP1350AVRLCDa | 815 | 1350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 249 | 99 | 351 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.86 |  | 96.9 |  | 97.9 |  | 98.2 |  | 98.2 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | CP1350AVRLCDa | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-04-01 | 2016-04-06 | United States, Canada | ES_1095904_CP1350AVRLCDa_04132016092300_9380447
2269035 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UHV | OL3000RTXL2UHV |  | Ac-output UPS | Static | OL3000RTXL2UHV | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 50-60 | 220-240 | 50-60 | No |  | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 46.72 | 43.84 | 88.7 | 93.6 | 91.1 | 96.1 | 91.4 | 96.8 | 91.6 | 97.2 | 91.3 | 96.1 | [7 empty] | 0.99 | 0.99 | [21 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 9 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2016-05-19 | United States, Europe, Taiwan, Japan, Canada | ES_1095904_OL3000RTXL2UHV_06042016092923_2563045
2269773 | CyberPower Systems, Inc. | CyberPower | OR1000PFCRT2U | OR1000PFCRT2U |  | Ac-output UPS | Static | OR1000PFCRT2U | 700 | 1000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 433 | 88 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.28 |  | 96.8 |  | 97.7 |  | 97.8 |  | 96.8 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2016-05-09 | United States, Canada | ES_1095904_OR1000PFCRT2U_06152016082436_9076848
2269774 | CyberPower Systems, Inc. | CyberPower | OR1500PFCRT2U | OR1500PFCRT2U |  | Ac-output UPS | Static | OR1500PFCRT2U | 1050 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 433 | 88 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.18 |  | 97.4 |  | 97.4 |  | 96.9 |  | 96.3 |  | 96.8 | [8 empty] | 0.99 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2016-05-09 | United States, Canada | ES_1095904_OR1500PFCRT2U_06152016082458_9098560
2269775 | CyberPower Systems, Inc. | CyberPower | OR2200PFCRT2U | OR2200PFCRT2U |  | Ac-output UPS | Static | OR2200PFCRT2U | 1540 | 2000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 433 | 88 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.27 |  | 98 |  | 97.8 |  | 97.5 |  | 96.6 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 13 | 1 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2016-05-09 | United States, Canada | ES_1095904_OR2200PFCRT2U_06152016082519_9119304
2273925 | CyberPower Systems, Inc. | CyberPower | CP1500AVRLCDa | CP1500AVRLCDa |  | Ac-output UPS | Static | BRG1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 108-132 | 59-61 | No |  | 277 | 99 | 356 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.67 |  | 96.3 |  | 97.6 |  | 97.6 |  | 97.5 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 2 | http://www.cyberpowersystems.com/ |  | Serial Port,Other,USB Port | None |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-07-15 | 2016-04-26 | United States, Canada | ES_1095904_CP1500AVRLCDa_04262016033216_1536209
2312821 | CyberPower Systems, Inc. | CyberPower | PR750ERTXL2U | PR750ERTXL2U | ELITE PRO 750ERT2U,ELITE PRO 750ERT2U,; ELITE PRO 750ERTXL2U,ELITE PRO 750ERTXL2U,; PR7500ERTXL2U JP,PR7500ERTXL2U JP,; PR750ERT2U JP,PR750ERT2U JP,; PR750ERT2U,PR750ERT2U, | Ac-output UPS | Static | PR750ERTXL2U | 750 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 87 | 433 | 412 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 50 | 230 | 50 | 0.63 |  | 98.1 |  | 98.3 |  | 98.6 |  | 98.6 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 10 | 27 | 1 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,SNMP (v1, 2 or 3),HTTP | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-03-01 | 2018-01-24 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR750ERTXL2U_03182018131033_8633530
2312822 | CyberPower Systems, Inc. | CyberPower | PR2200ERTXL2U | PR2200ERTXL2U | ELITE PRO 1000ERT2U,ELITE PRO 1000ERT2U,; ELITE PRO 1000ERTXL2U,ELITE PRO 1000ERTXL2U,; ELITE PRO 1500ERT2U,ELITE PRO 1500ERT2U,; ELITE PRO 1500ERTXL2U,ELITE PRO 1500ERTXL2U,; ELITE PRO 2000ERT2U,ELITE PRO 2000ERT2U,; ELITE PRO 2000ERTXL2U,ELITE PRO 2000ERTXL2U,; ELITE PRO 2200ERT2U,ELITE PRO 2200ERT2U,; ELITE PRO 2200ERTXL2U,ELITE PRO 2200ERTXL2U,; PR1000ERT2U JP,PR1000ERT2U JP,; PR1000ERT2U,PR1000ERT2U,; PR1000ERTXL2U JP,PR1000ERTXL2U JP,; PR1000ERTXL2U,PR1000ERTXL2U,; PR1500ERT2U JP,PR1500ERT2U JP,; PR1500ERT2U,PR1500ERT2U,; PR1500ERTXL2U JP,PR1500ERTXL2U JP,; PR1500ERTXL2U,PR1500ERTXL2U,; PR2000ERT2U JP,PR2000ERT2U JP,; PR2000ERT2U,PR2000ERT2U,; PR2000ERTXL2U JP,PR2000ERTXL2U JP,; PR2000ERTXL2U,PR2000ERTXL2U,; PR2200ERT2U JP,PR2200ERT2U JP,; PR2200ERT2U,PR2200ERT2U,; PR2200ERTXL2U JP,PR2200ERTXL2U JP, | Ac-output UPS | Static | PR2200ERTXL2U | 2200 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 87 | 433 | 500 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 50 | 230 | 50 | 0.004 |  | 98.7 |  | 98.7 |  | 98.5 |  | 98.4 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2017-11-01 | 2018-01-24 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR2200ERTXL2U_03182018133339_0019820
2320691 | CyberPower Systems, Inc. | CyberPower | SE450G1 | SE450G1 |  | Ac-output UPS | Static | SE450G1 | 260 | 450 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 210 | 115 | 81 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.92 |  | 95.5 |  | 97.9 |  | 98.4 |  | 98.5 |  | 97.8 | [31 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 6 | 3 | N/A |  | None | None |  | No |  | N/A | N/A | 2018-05-15 | 2018-04-11 | United States | ES_1095904_SE450G1_05202018125226_0746423
2320693 | CyberPower Systems, Inc. | CyberPower | SX650U | SX650U |  | Ac-output UPS | Static | SX650U | 360 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 250 | 147 | 82 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.89 |  | 96.8 |  | 98.3 |  | 98.6 |  | 98.8 |  | 98.3 | [31 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 3 | N/A |  | USB Port | None |  | No |  | N/A | N/A | 2018-05-15 | 2018-04-11 | United States | ES_1095904_SX650U_05202018130014_1214363
2320694 | CyberPower Systems, Inc. | CyberPower | ST425 | ST425 |  | Ac-output UPS | Static | SE450G1 | 260 | 425 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 210 | 115 | 81 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.92 |  | 95.5 |  | 97.9 |  | 98.4 |  | 98.5 |  | 97.8 | [31 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 6 | 3 | N/A |  | None | None |  | No |  | N/A | N/A | 2018-06-15 | 2018-04-11 | United States | ES_1095904_ST425_05202018125627_0987495
2320695 | CyberPower Systems, Inc. | CyberPower | ST625U | ST625U |  | Ac-output UPS | Static | SX650U | 360 | 625 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 250 | 147 | 82 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.89 |  | 96.8 |  | 98.3 |  | 98.6 |  | 98.8 |  | 98.3 | [31 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 3 | N/A |  | USB Port | None |  | No |  | N/A | N/A | 2018-06-15 | 2018-04-11 | United States | ES_1095904_ST625U_05202018130322_1402935
2320696 | CyberPower Systems, Inc. | CyberPower | SX950U | SX950U |  | Ac-output UPS | Static | SX950U | 510 | 950 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 310 | 178 | 80 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.18 |  | 97.4 |  | 98.5 |  | 98.7 |  | 98.5 |  | 98.4 | [31 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 3 | N/A |  | USB Port | None |  | No |  | N/A | N/A | 2018-05-15 | 2018-04-11 | United States | ES_1095904_SX950U_05202018130453_1493920
2320697 | CyberPower Systems, Inc. | CyberPower | ST900U | ST900U |  | Ac-output UPS | Static | SX950U | 500 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 310 | 178 | 80 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.18 |  | 97.4 |  | 98.5 |  | 98.7 |  | 98.5 |  | 98.4 | [31 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 3 | N/A |  | USB Port | None |  | No |  | N/A | N/A | 2018-06-15 | 2018-04-11 | United States | ES_1095904_ST900U_05202018130758_1678289
2321480 | CyberPower Systems, Inc. | CyberPower | PR750RTXL2U | PR750RTXL2U | PR750RT2U JP,PR750RT2U JP,; PR750RT2U,PR750RT2U,; PR750RTXL2U JP,PR750RTXL2U JP, | Ac-output UPS | Static | PR750RTXL2U | 750 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 87 | 433 | 412 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.61 |  | 97.7 |  | 98.4 |  | 98.6 |  | 98.6 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 11 | 29 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-07-01 | 2018-06-08 | United States, Taiwan, Japan, Canada | ES_1095904_PR750RTXL2U_06212018104718_8038734
2321481 | CyberPower Systems, Inc. | CyberPower | PR1500RTXL2U | PR1500RTXL2U | PR1000RT2U JP,PR1000RT2U JP,; PR1000RT2U,PR1000RT2U,; PR1000RTXL2U JP,PR1000RTXL2U JP,; PR1000RTXL2U,PR1000RTXL2U,; PR1500RT2U JP,PR1500RT2U JP,; PR1500RT2U,PR1500RT2U, | Ac-output UPS | Static | PR1500RTXL2U | 1500 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 87 | 433 | 500 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.98 |  | 98.3 |  | 98.4 |  | 98.6 |  | 98.4 |  | 98.5 | [31 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7 | 19 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-07-01 | 2018-06-08 | United States, Taiwan, Japan, Canada | ES_1095904_PR1500RTXL2U_06212018104839_8119638
2321482 | CyberPower Systems, Inc. | CyberPower | PR2000RTXL2U | PR2000RTXL2U | PR2000RT2U JP,PR2000RT2U JP,; PR2000RT2U,PR2000RT2U, | Ac-output UPS | Static | PR2000RTXL2U | 2000 | 2000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 87 | 433 | 500 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.37 |  | 98.3 |  | 98.4 |  | 98.1 |  | 97.8 |  | 98 | [31 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4 | 13 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-07-01 | 2018-06-08 | United States, Taiwan, Japan, Canada | ES_1095904_PR2000RTXL2U_06212018110131_8891341
2322460 | CyberPower Systems, Inc. | CyberPower | CP1500AVRTa | CP1500AVRTa | CP1200AVRa,CP1200AVRa,; CP900AVRa,CP900AVRa, | Ac-output UPS | Static | CP1500AVRTa | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 350 | 190 | 438 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.79 |  |  |  | 98.7 |  | 98.8 |  | 98.8 |  | 98.8 | [31 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-10-01 | 2018-07-09 | United States | ES_1095904_CP1500AVRTa_07112018064639_1599831
2323355 | CyberPower Systems, Inc. | CyberPower | PR3000RTXL2UHVA | PR3000RTXL2UHVA | ELITE PRO 2200ERTXL2UA,ELITE PRO 2200ERTXL2UA,; ELITE PRO 3000ERT2U,ELITE PRO 3000ERT2U,; ELITE PRO 3000ERTXL2U,ELITE PRO 3000ERTXL2U,; ELITE PRO 3000ERTXL2UA,ELITE PRO 3000ERTXL2UA,; PR2200ERTXL2UA JP,PR2200ERTXL2UA JP,; PR2200ERTXL2UA,PR2200ERTXL2UA,; PR2200RTXL2UHVA JP,PR2200RTXL2UHVA JP,; PR2200RTXL2UHVA,PR2200RTXL2UHVA,; PR3000ERT2U JP,PR3000ERT2U JP,; PR3000ERT2U,PR3000ERT2U,; PR3000ERTXL2U JP,PR3000ERTXL2U JP,; PR3000ERTXL2U,PR3000ERTXL2U,; PR3000ERTXL2UA JP,PR3000ERTXL2UA JP,; PR3000ERTXL2UA,PR3000ERTXL2UA,; PR3000RTXL2UHVA JP,PR3000RTXL2UHVA JP,; PX2200ERTXL2U,PX2200ERTXL2U,; PX3000ERTXL2U,PX3000ERTXL2U, | Ac-output UPS | Static | PR3000RTXL2UHVA | 3000 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 433 | 630 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 50 | 230 | 50 | 5.8 |  | 99.1 |  | 99 |  | 98.9 |  | 98.8 |  | 98.9 | [31 empty] | 98.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-08-01 | 2018-07-13 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR3000RTXL2UHVA_07132018092130_3690657
2323356 | CyberPower Systems, Inc. | CyberPower | PR3000RTXL2UA | PR3000RTXL2UA | PR2200RT2U JP,PR2200RT2U JP,; PR2200RT2U,PR2200RT2U,; PR2200RTXL2U JP,PR2200RTXL2U JP,; PR2200RTXL2U,PR2200RTXL2U,; PR2200RTXL2UA JP,PR2200RTXL2UA JP,; PR2200RTXL2UA,PR2200RTXL2UA,; PR3000RT2U JP,PR3000RT2U JP,; PR3000RT2U,PR3000RT2U,; PR3000RTXL2U JP,PR3000RTXL2U JP,; PR3000RTXL2U,PR3000RTXL2U,; PR3000RTXL2UA JP,PR3000RTXL2UA JP, | Ac-output UPS | Static | PR3000RTXL2UA | 3000 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 87 | 433 | 630 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.4 |  | 99 |  | 99.1 |  | 98.9 |  | 98.5 |  | 98.8 | [31 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | TCP/IP, UDP | Yes |  | N/A | N/A | 2018-08-01 | 2018-07-13 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095904_PR3000RTXL2UA_07292018101208_9128733
2324678 | CyberPower Systems, Inc. | CyberPower | CP825AVRLCDa | CP825AVRLCDa | CP685AVRLCDa,CP685AVRLCDa,; CP685AVRa,CP685AVRa,; CP800AVRa,CP800AVRa, | Ac-output UPS | Static | CP825AVRLCDa | 450 | 850 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 169 | 88 | 28 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.792 |  | 97.4 |  | 98.6 |  | 99 |  | 99.2 |  | 98.9 | [31 empty] | 98.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 1 | 14 | 3 | N/A |  | USB Port,Ethernet | None |  | No |  | N/A | N/A | 2018-09-01 | 2018-08-22 | United States, Canada | ES_1095904_CP825AVRLCDa_08232018110113_2073585
2324679 | CyberPower Systems, Inc. | CyberPower | CP825LCDa | CP825LCDa | CP600LCDa,CP600LCDa, | Ac-output UPS | Static | CP825LCDa | 450 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 169 | 88 | 28 |  |  |  | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.992 |  | 97.2 |  | 98.3 |  | 98.7 |  | 98.8 |  | 98.4 | [31 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 1 | 14 | 3 | N/A |  | USB Port | None |  | No |  | N/A | N/A | 2018-09-01 | 2018-08-22 | United States, Canada | ES_1095904_CP825LCDa_08232018110527_2327669
2326399 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UHV | OL3000RTXL2UHV |  | Ac-output UPS | Static | OL3000RTXL2UHV | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 40.76 |  | 89.4 |  | 91.7 |  | 92.1 |  | 92.1 |  | 92 | [31 empty] | 92 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UHV_09192018081230_4750391
2326400 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UHVN | OL3000RTXL2UHVN |  | Ac-output UPS | Static | OL3000RTXL2UHV | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 40.76 |  | 89.4 |  | 91.7 |  | 92.1 |  | 92.1 |  | 92 | [31 empty] | 92 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UHVN_09192018081458_4898740
2326401 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UHVTAA | OL3000RTXL2UHVTAA |  | Ac-output UPS | Static | OL3000RTXL2UHV | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 40.76 |  | 89.4 |  | 91.7 |  | 92.1 |  | 92.1 |  | 92 | [31 empty] | 92 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2016-06-10 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UHVTAA_09192018081521_4921202
2326402 | CyberPower Systems, Inc. | CyberPower | OL3000RT JP | OL3000RT JP |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RT JP_09192018083554_6154513
2326403 | CyberPower Systems, Inc. | CyberPower | OL3000RTN JP | OL3000RTN JP |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RTN JP_09192018083920_6360648
2326404 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2U | OL3000RTXL2U |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2U_09192018083457_6097421
2326405 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UN | OL3000RTXL2UN |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UN_09192018083824_6304201
2326406 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UNTAA | OL3000RTXL2UNTAA |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UNTAA_09192018084003_6403514
2326407 | CyberPower Systems, Inc. | CyberPower | OL3000RTXL2UTAA | OL3000RTXL2UTAA |  | Ac-output UPS | Static | OL3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.93 |  | 89.8 |  | 91.7 |  | 91.6 |  | 91.2 |  | 91.5 | [31 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL3000RTXL2UTAA_09192018083710_6230829
2326408 | CyberPower Systems, Inc. | CyberPower | OL2200RT JP | OL2200RT JP |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RT JP_09192018091410_8450103
2326409 | CyberPower Systems, Inc. | CyberPower | OL2200RTN JP | OL2200RTN JP |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RTN JP_09192018091638_8598840
2326410 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2U | OL2200RTXL2U |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RTXL2U_09192018090628_7988895
2326411 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2UN | OL2200RTXL2UN |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RTXL2UN_09192018091604_8564752
2326412 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2UNTAA | OL2200RTXL2UNTAA |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RTXL2UNTAA_09192018091706_8626638
2326413 | CyberPower Systems, Inc. | CyberPower | OL2200RTXL2UTAA | OL2200RTXL2UTAA |  | Ac-output UPS | Static | OL2200RTXL2U | 1800 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.86 |  | 89.6 |  | 91.9 |  | 92 |  | 91.9 |  | 91.9 | [31 empty] | 91.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL2200RTXL2UTAA_09192018091503_8503509
2326414 | CyberPower Systems, Inc. | CyberPower | OL1500RT JP | OL1500RT JP |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RT JP_09192018094642_0402177
2326415 | CyberPower Systems, Inc. | CyberPower | OL1500RTN JP | OL1500RTN JP |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RTN JP_09192018094805_0485735
2326416 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2U | OL1500RTXL2U |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RTXL2U_09192018094530_0330175
2326417 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2UN | OL1500RTXL2UN |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RTXL2UN_09192018094558_0358658
2326418 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2UNTAA | OL1500RTXL2UNTAA |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RTXL2UNTAA_09192018094841_0521558
2326419 | CyberPower Systems, Inc. | CyberPower | OL1500RTXL2UTAA | OL1500RTXL2UTAA |  | Ac-output UPS | Static | OL1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 23.59 |  | 88.7 |  | 91.1 |  | 91 |  | 90.6 |  | 90.9 | [31 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1500RTXL2UTAA_09192018094730_0450075
2326420 | CyberPower Systems, Inc. | CyberPower | OL1000RT JP | OL1000RT JP |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RT JP_09192018100057_1257619
2326421 | CyberPower Systems, Inc. | CyberPower | OL1000RTN JP | OL1000RTN JP |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RTN JP_09192018100254_1374890
2326422 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2U | OL1000RTXL2U |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RTXL2U_09192018100004_1204376
2326423 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2UN | OL1000RTXL2UN |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RTXL2UN_09192018100209_1329811
2326424 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2UNTAA | OL1000RTXL2UNTAA |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RTXL2UNTAA_09192018100332_1412378
2326425 | CyberPower Systems, Inc. | CyberPower | OL1000RTXL2UTAA | OL1000RTXL2UTAA |  | Ac-output UPS | Static | OL1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 433 | 430 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.02 |  | 85.4 |  | 90.1 |  | 91.3 |  | 91.8 |  | 91.1 | [31 empty] | 91.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 3 | http://www.cyberpowersystems.com/ |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes |  | http://www.cyberpowersystems.com | http://www.cyberpowersystems.com/ | 2013-07-01 | 2018-09-19 | United States | ES_1095904_OL1000RTXL2UTAA_09192018100133_1293976
2331551 | CyberPower Systems, Inc. | CyberPower | CST150XLU | CST150XLU | CST150XLUTAA,CST150XLUTAA, | Ac-output UPS | Static | LX1500GU | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 249 | 99 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.9 |  | 97.6 |  | 98.5 |  | 98.7 |  | 98.6 |  | 98.6 | [31 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 3 | N/A |  | USB Port | Other | HID | Yes |  | https://www.cyberpowersystems.com/product/ups/lx1500gu/ | N/A | 2016-04-01 | 2018-12-17 | United States, Canada | ES_1095904_CST150XLU_12172018062029_7629946
2331552 | CyberPower Systems, Inc. | CyberPower | LX1500GU | LX1500GU | CP1350AVRLCDa,CP1350AVRLCDa,; CP1350AVRLCDaTAA,CP1350AVRLCDaTAA,; CST135XLU,CST135XLU,; CST135XLUTAA,CST135XLUTAA,; LX1100G,LX1100G,; LX1100GTAA,LX1100GTAA,; LX1325GU,LX1325GU,; LX1325GUTAA,LX1325GUTAA,; LX1500GUTAA,LX1500GUTAA, | Ac-output UPS | Static | LX1500GU | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 249 | 99 | 348 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.9 |  | 97.6 |  | 98.5 |  | 98.7 |  | 98.6 |  | 98.6 | [31 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 3 | N/A |  | USB Port | Other | HID | Yes |  | https://www.cyberpowersystems.com/product/ups/lx1500gu/ | N/A | 2014-06-27 | 2018-12-17 | United States, Canada | ES_1095904_LX1500GU_12172018061850_7530066
2331554 | CyberPower Systems, Inc. | CyberPower | BRG1500AVRLCD | BRG1500AVRLCD | BRG1350AVRLCD,BRG1350AVRLCD,; BRG1350AVRLCDTAA,BRG1350AVRLCDTAA,; BRG1500AVRLCDTAA,BRG1500AVRLCDTAA, | Ac-output UPS | Static | BRG1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 279 | 99 | 356 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.7 |  | 97.4 |  | 98.4 |  | 98.7 |  | 98.7 |  | 98.6 | [31 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 3 | N/A |  | Serial Port,USB Port | Other | HID CyberPower serial Protocol (v2) | Yes |  | https://www.cyberpowersystems.com/product/ups/brg1500avrlcd/ | N/A | 2014-05-15 | 2018-12-17 | United States, Canada | ES_1095904_BRG1500AVRLCD_12172018072717_1637139
2331555 | CyberPower Systems, Inc. | CyberPower | CP1500AVRLCDa | CP1500AVRLCDa | CP1500AVRLCDaTAA,CP1500AVRLCDaTAA, | Ac-output UPS | Static | BRG1500AVRLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 279 | 99 | 356 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.7 |  | 97.4 |  | 98.4 |  | 98.7 |  | 98.7 |  | 98.6 | [31 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 12 | 3 | N/A |  | Serial Port,USB Port | Other | HID CyberPower serial Protocol (v2) | Yes |  | https://www.cyberpowersystems.com/product/ups/brg1500avrlcd/ | N/A | 2016-07-15 | 2018-12-17 | United States, Canada | ES_1095904_CP1500AVRLCDa_12172018072831_1711775
2331669 | CyberPower Systems, Inc. | CyberPower | CPS1500AVRa | CPS1500AVRa | CPS1500AVRaTAA,CPS1500AVRaTAA, | Ac-output UPS | Static | OR1500LCDRT2U | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 88 | 438 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.5 |  | 98.3 |  | 98.9 |  | 99 |  | 98.9 |  | 98.9 | [31 empty] | 98.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 18 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | HID, CyberPower serial Protocol (v2) | Yes |  | https://www.cyberpowersystems.com/product/ups/or1500lcdrt2u/ | N/A | 2013-09-18 | 2018-12-19 | United States, Canada | ES_1095904_CPS1500AVRa_12192018072533_4333622
2331670 | CyberPower Systems, Inc. | CyberPower | OR1500LCDRT2U | OR1500LCDRT2U | OR1500LCDRT2UN,OR1500LCDRT2UN,; OR1500LCDRT2UNTAA,OR1500LCDRT2UNTAA,; OR1500LCDRT2UTAA,OR1500LCDRT2UTAA, | Ac-output UPS | Static | OR1500LCDRT2U | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 88 | 438 | 400 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.5 |  | 98.3 |  | 98.9 |  | 99 |  | 98.9 |  | 98.9 | [31 empty] | 98.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 18 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | HID, CyberPower serial Protocol (v2) | Yes |  | https://www.cyberpowersystems.com/product/ups/or1500lcdrt2u/ | N/A | 2013-09-18 | 2018-12-19 | United States, Canada | ES_1095904_OR1500LCDRT2U_12192018072131_4091351
2331671 | CyberPower Systems, Inc. | CyberPower | CP1000PFCLCD | CP1000PFCLCD | CP1000PFCLCDTAA,CP1000PFCLCDTAA,; CP850PFCLCD,CP850PFCLCD,; CP850PFCLCDTAA,CP850PFCLCDTAA, | Ac-output UPS | Static | CP1000PFCLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 231 | 99 | 264 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.1 |  | 97.8 |  | 98.6 |  | 98.9 |  | 99 |  | 98.8 | [31 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 9 | 3 | N/A |  | Serial Port,USB Port | Other | HID | Yes |  | https://www.cyberpowersystems.com/product/ups/cp1000pfclcd/ | N/A | 2012-07-04 | 2018-12-19 | United States, Canada | ES_1095904_CP1000PFCLCD_12192018075623_6183427
2331672 | CyberPower Systems, Inc. | CyberPower | CP1500PFCLCD | CP1500PFCLCD | CP1350PFCLCD,CP1350PFCLCD,; CP1350PFCLCDTAA,CP1350PFCLCDTAA,; CP1500PFCLCDTAA,CP1500PFCLCDTAA, | Ac-output UPS | Static | CP1500PFCLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 264 | 99 | 361 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4 |  | 97.8 |  | 98.6 |  | 98.8 |  | 98.8 |  | 98.7 | [31 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 11 | 3 | N/A |  | Serial Port,USB Port | Other | HID | Yes |  | https://www.cyberpowersystems.com/product/ups/cp1500pfclcd/ | N/A | 2012-07-04 | 2018-12-19 | United States, Canada | ES_1095904_CP1500PFCLCD_12192018081032_7032376
2233237 | CyberPower Systems, Inc. | WBOX | 0E-1000V9VRD | 0E-1000V9VRD |  | Ac-output UPS | Static | CP1000AVRLCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 114-126 | 60-61 | No |  | 225 | 110 | 260 | 9 | 5 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.94 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.7 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 1 | 6 | 1 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2009-01-15 | 2015-02-04 | United States | ES_1095904_0E-1000V9VRD_02172015081215_70022327
2233392 | CyberPower Systems, Inc. | WBOX | 0E-1500V8VRD | 0E-1500V8VRD |  | Ac-output UPS | Static | CP1500PFCLCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 90-140 | 57-63 | 102-138 | 57-63 | No |  | 264 | 99 | 361 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6 |  | 97.8 |  | 98.5 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3 | 11 | 2 | N/A |  | Serial Port,USB Port | Other | RS232 | Yes |  | http://www.cpsww.com/ | N/A | 2012-07-04 | 2012-10-19 | United States | ES_1095904_0E-1500V8VRD_02192015030236_70022334
2301944 | Delta Electronics, Inc. Tainan Branch | Delta | HPH 20K-LV-B | HPH 20K-LV-B | HPH 20K-LV-B/N,HPH 20K-LV-B/N, | Ac-output UPS | Static | HPH 20K-LV-B | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1380 | 520 | 800 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 220 | 60 | 220 | 60 | 404.49 |  | 92.6 |  | 93.9 |  | 93.2 |  | 96.7 |  | 93.4 | [8 empty] | 1 | [22 empty] | 93.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5Min12S | 15Min24S | 2 Year | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) |  | No |  | Not available due to product not ready yet. | N/A | 2017-08-01 | 2017-08-10 | United States, Europe, Canada | ES_1140198_HPH 20K-LV-B_08102017073900_0740566
2301945 | Delta Electronics, Inc. Tainan Branch | Delta | HPH 30K-LV-B | HPH 30K-LV-B | HPH 30K-LV-B/N,HPH 30K-LV-B/N, | Ac-output UPS | Static | HPH 30K-LV-B | 30000 | 30000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1380 | 520 | 800 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 220 | 60 | 220 | 60 | 431.95 |  | 93.1 |  | 94.2 |  | 93.4 |  | 96.4 |  | 93.7 | [8 empty] | 1 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 5Min31S | 15Min42S | 2 Year | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) |  | No |  | Not available due to product not ready yet. | N/A | 2017-08-01 | 2017-08-10 | United States, Europe, Canada | ES_1140198_HPH 30K-LV-B_08102017073925_0765803
2301946 | Delta Electronics, Inc. Tainan Branch | Delta | HPH 40K-LV-B | HPH 40K-LV-B | HPH 40K-LV-B/N,HPH 40K-LV-B/N, | Ac-output UPS | Static | HPH 40K-LV-B | 40000 | 40000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1760 | 520 | 800 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 220 | 60 | 220 | 60 | 789.04 |  | 93 |  | 94.3 |  | 92.7 |  | 95.4 |  | 93.6 | [8 empty] | 1 | [22 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3Min40S | 11Min10S | 2 Year | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) |  | No |  | Not available due to product not ready yet. | N/A | 2017-08-01 | 2017-08-10 | United States, Europe, Canada | ES_1140198_HPH 40K-LV-B_08102017073946_0786787
2301947 | Delta Electronics, Inc. Tainan Branch | Delta | HPH 60K-LV-B | HPH 60K-LV-B | HPH 60K-LV-B/N,HPH 60K-LV-B/N, | Ac-output UPS | Static | HPH 60K-LV-B | 60000 | 60000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1760 | 520 | 800 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 220 | 60 | 220 | 60 | 1048.94 |  | 93.2 |  | 94.1 |  | 93.7 |  | 95.9 |  | 93.8 | [8 empty] | 1 | [22 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 3Min04S | 9Min35S | 2 Year | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) |  | No |  | Not available due to product not ready yet. | N/A | 2017-08-01 | 2017-08-10 | United States, Europe, Canada | ES_1140198_HPH 60K-LV-B_08102017074010_0810164
2307357 | Delta Electronics, Inc. Tainan Branch | Delta | UPS824DM | UPS824DM |  | Ac-output UPS | Static | UPS824DM | 742000 | 825000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 50-60 | 480-480 | 50-60 | Yes | 1 | 1900 | 2745 | 875 |  |  |  | Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10900 |  | 94.1 |  | 95.6 |  | 95.7 |  | 95.1 |  | 95.2 | [31 empty] | 95.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 7.5 | 20.3 | 5 | N/A |  | Serial Port,USB Port,Ethernet | Other,HTTP,SNMP (v1, 2 or 3) |  | No |  | N/A | N/A | 2018-03-01 | 2017-12-05 | United States, Europe, Canada | ES_1140198_UPS824DM_12052017073300_9180608
2325951 | Delta Electronics, Inc. Tainan Branch | Delta | RT-1K | RT-1K |  | Ac-output UPS | Static | RT-1K | 900 | 1000 | RT-1K |  |  | Double Conversion | ac - Double Conversion (VFI) | Consumer | 100-120 | 50-60 | 100-120 | 50-60 | Yes |  | 88 | 440 | 335 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.69 |  | 97.8 |  | 89.4 |  | 90.6 |  | 90.7 |  | 90.2 | [31 empty] | 90.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-09-11 | United States, Taiwan, Canada | ES_1140198_RT-1K_09112018052501_3501027
2325952 | Delta Electronics, Inc. Tainan Branch | Delta | RT-2K | RT-2K |  | Ac-output UPS | Static | RT-2K | 1800 | 2000 | RT-2K |  |  | Double Conversion | ac - Double Conversion (VFI) | Consumer | 100-120 | 50-60 | 100-120 | 50-60 | Yes |  | 88 | 440 | 430 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 35.94 |  | 90 |  | 92.1 |  | 92.5 |  | 92 |  | 92.2 | [31 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-09-08 | United States, Taiwan, Canada | ES_1140198_RT-2K_09162018074236_3756430
2325955 | Delta Electronics, Inc. Tainan Branch | Delta | RT-1.5K | RT-1.5K |  | Ac-output UPS | Static | RT-1.5K | 1350 | 1500 | RT-1.5K |  |  | Double Conversion | ac - Double Conversion (VFI) | Consumer | 100-120 | 50-60 | 100-120 | 50-60 | Yes |  | 88 | 440 | 430 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 33.72 |  | 88.2 |  | 90.9 |  | 91.4 |  | 91.2 |  | 91.2 | [31 empty] | 91.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-09-14 | United States, Taiwan, Canada | ES_1140198_RT-1.5K_09142018025605_3765908
2326091 | Delta Electronics, Inc. Tainan Branch | Delta | RT-3K | RT-3K |  | Ac-output UPS | Static | RT-3K | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Consumer | 100-120 | 50-60 | 100-120 | 50-60 | Yes |  | 88 | 440 | 565 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 53.656 |  | 87.4 |  | 91.4 |  | 92.3 |  | 92.1 |  | 92 | [31 empty] | 92 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-09-19 | United States, Taiwan, Canada | ES_1140198_RT-3K_09192018065205_9925142
2327102 | Delta Electronics, Inc. Tainan Branch | Delta | RT-10K | RT-10K |  | Ac-output UPS | Static | RT-10K | 10000 | 10000 | RT-10K |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 176 | 440 | 665 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 111.03 |  | 94.3 |  | 94.9 |  | 95.4 |  | 95.2 |  | 95.2 | [31 empty] | 95.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-10-05 | United States, Taiwan, Canada | ES_1140198_RT-10K_10052018083627_8587153
2327103 | Delta Electronics, Inc. Tainan Branch | Delta | RT-8K | RT-8K |  | Ac-output UPS | Static | RT-8K | 8000 | 8000 | RT-8K |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 176 | 440 | 665 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 61.92 |  | 94.1 |  | 94.2 |  | 94.6 |  | 94.8 |  | 94.5 | [31 empty] | 94.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 15 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-10-05 | United States, Taiwan, Canada | ES_1140198_RT-8K_10052018083646_8606062
2330293 | Delta Electronics, Inc. Tainan Branch | Delta | RT-6K | RT-6K | RT-5K,RT-5K, | Ac-output UPS | Static | RT-6K | 6000 | 6000 | RT-6K |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 4 | 176 | 440 | 665 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 55.9 |  | 92.7 |  | 94.4 |  | 94.5 |  | 94.1 |  | 94.3 | [31 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | N/A | 2 | 9 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other | USB HID Power Devices | No |  | N/A | N/A | 2018-11-01 | 2018-11-28 | United States, Taiwan, Canada | ES_1140198_RT-6K_11282018055911_4751980
2148912 | Eaton Corporation | EATON | 9SX5KiRT | 9SX5KiRT | 9PX5K,9PX5K,models are identical excpet front panel color, outlts, and parallel connectors; 9SX5KiRT,9SX5KiRT,models are identical excpet front panel color, outlts, and parallel connectors | Ac-output UPS | Static | 9PX5Ki | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 5 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 93.95 |  | 88.9 |  | 92.4 |  | 93.5 |  | 93.8 |  | 93.3 | [8 empty] | 0.99 | [22 empty] | 93.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 71 | 177 | 2 | http://powerquality.eaton.com/products-services/backup-power-ups/9px.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/products-services/backup-power-ups/9px.aspx?cx=3 | N/A | 2012-11-21 | 2012-11-21 | United States, Europe | ES_29597_9SX5KiRT_11212012080149_1152622
2148914 | Eaton Corporation | EATON | 9PX5K | 9PX5K | 9PX5Ki,9PX5Ki,models are identical except front panel color, outlets, and parallel connectors; 9SX5KiRT,9SX5KiRT,models are identical except front panel color, outlets, and parallel connectors | Ac-output UPS | Static | 9PX5Ki | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 5 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 93.95 |  | 88.9 |  | 92.4 |  | 93.5 |  | 93.8 |  | 93.3 | [8 empty] | 0.99 | [22 empty] | 93.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 71 | 177 | 2 | HTTP://POWERQUALITY.EATON.COM/PRODUCTS-SERVICES/BACKUP-POWER-UPS/9PX.ASPX?CX=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | HTTP://POWERQUALITY.EATON.COM/PRODUCTS-SERVICES/BACKUP-POWER-UPS/9PX.ASPX?CX=3 | N/A | 2012-11-21 | 2012-11-21 | United States, Europe | ES_29597_9PX5K_11212012091434_5391791
2149137 | Eaton Corporation | EATON | 9SX6KiRT, 9PX6K, 9PX6Ki, 9PX6KG | 9SX6KiRT, 9PX6K, 9PX6Ki, 9PX6KG |  | Ac-output UPS | Static | 9PX6Ki | 5400 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 5 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 93.95 |  | 90.3 |  | 93.2 |  | 93.8 |  | 93.8 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 69 | 177 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2012-12-01 | 2012-11-28 | United States, Europe | ES_29597_9SX6KiRT, 9PX6K, 9PX6Ki, 9PX6KG_11282012095944_4182558
2149139 | Eaton Corporation | EATON | 9SX8KiPM, 9PX8KPM, 9PX8KiPM | 9SX8KiPM, 9PX8KPM, 9PX8KiPM |  | Ac-output UPS | Static | 9PX8KiPM | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 99.84 |  | 92.4 |  | 94.4 |  | 94.7 |  | 94.6 |  | 94.6 | [8 empty] | 0.99 | [22 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 66 | 141 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2012-12-01 | 2012-11-28 | United States, Europe | ES_29597_9SX8KiPM, 9PX8KPM, 9PX8KiPM_11282012113025_9682243
2149142 | Eaton Corporation | EATON | 9SX11KiPM, 9PX11KPM, 9PX11KiPM | 9SX11KiPM, 9PX11KPM, 9PX11KiPM |  | Ac-output UPS | Static | 9PX11KiPM | 10000 | 11000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 107.02 |  | 93.6 |  | 94.8 |  | 95 |  | 94.8 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 39 | 94 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2012-12-01 | 2012-11-28 | United States, Europe | ES_29597_9SX11KiPM, 9PX11KPM, 9PX11KiPM_11282012114121_9232973
2149147 | Eaton Corporation | EATON | 5PX1500RT,5P1500RT | 5PX1500RT,5P1500RT |  | Ac-output UPS | Static | 5PX1500RT | 1440 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 86 | 441 | 522 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 22.3 |  | 94.9 |  | 96.9 |  | 97.1 |  | 97.2 |  | 97.1 | [8 empty] | 0.99 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 8 | 2 | http://powerquality.eaton.com/Products-services/ |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/ | N/A | 2012-12-01 | 2012-11-28 | United States, Japan, Canada | ES_29597_5PX1500RT,5P1500RT_11282012124642_8581269
2149148 | Eaton Corporation | EATON | 5PX2200RT, 5P2200RT | 5PX2200RT, 5P2200RT |  | Ac-output UPS | Static | 5PX2200RT | 1920 | 1950 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 86 | 441 | 522 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 21.89 |  | 96.2 |  | 97.2 |  | 97.4 |  | 97.3 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 8 | 2 | http://powerquality.eaton.com/5PX2200RT.aspx?CX=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/5PX2200RT.aspx?CX=3 | N/A | 2012-12-01 | 2012-11-28 | United States, Japan, Canada | ES_29597_ 5PX2200RT, 5P2200RT_11282012132130_5222867
2149149 | Eaton Corporation | EATON | 5PX3000RT2U, 5PX3000RT3U, 5P3000 | 5PX3000RT2U, 5PX3000RT3U, 5P3000 |  | Ac-output UPS | Static | 5PX3000RT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 3 | 130 | 441 | 647 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 28.62 |  | 96.4 |  | 97.4 |  | 97.5 |  | 97.1 |  | 97.4 | [8 empty] | 0.99 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 8 | 2 | http://powerquality.eaton.com/Products-services/ |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/5PX.aspx?cx=3 | N/A | 2012-12-01 | 2012-11-28 | United States, Japan, Canada | ES_29597_5PX3000RT2U, 5PX3000RT3U, 5P3000 _11282012134038_4005182
2150658 | Eaton Corporation | EATON | 9SX8KiPM, 9PXTFMR11, 9PX8KPM, 9PXTFMR11, 9PX8KiPM, 9PXTFMR11 | 9SX8KiPM, 9PXTFMR11, 9PX8KPM, 9PXTFMR11, 9PX8KiPM, 9PXTFMR11 |  | Ac-output UPS | Static | 9SX8KiPM, 9PXTFMR11 | 6900 | 7700 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-250 | 50-60 | 120-240 | 50-60 | Yes | 6 | 260 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 219.5 |  | 86.4 |  | 90.9 |  | 91.5 |  | 91.5 |  | 91.3 | [8 empty] | 0.99 | [22 empty] | 91.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 66 | 141 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2012-12-05 | 2012-12-03 | United States, Europe | ES_29597_9SX8KiPM, 9PXTFMR11, 9PX8KPM, 9PXTFMR11, 9PX8KiPM, 9PXTFMR11_12032012164755_1466240
2150663 | Eaton Corporation | EATON | 9SX11KiPM, 9PXTFMR11, 9PX11KPM, 9PXTFMR11, 9PX11KiPM, 9PXTFMR11 | 9SX11KiPM, 9PXTFMR11, 9PX11KPM, 9PXTFMR11, 9PX11KiPM, 9PXTFMR11 |  | Ac-output UPS | Static | 9PX11KiPM, 9PXTFMR11 | 10000 | 11000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-250 | 50-60 | 120-240 | 50-60 | Yes | 6 | 260 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 219.9 |  | 89 |  | 91.8 |  | 92 |  | 91.5 |  | 91.8 | [8 empty] | 0.99 | [22 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 39 | 94 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | None | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2012-12-06 | 2012-12-04 | United States, Europe | ES_29597_9SX11KiPM, 9PXTFMR11, 9PX11KPM, 9PXTFMR11, 9PX11KiPM, 9PXTFMR11_12042012082257_6184487
2194420 | Eaton Corporation | EATON | EATON 3S750 | EATON 3S750 |  | Ac-output UPS | Static | EATON 3S750 | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | No |  | 86 | 170 | 335 | 10 | 1 | 0 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 6.2 |  | 96.4 |  | 97.8 |  | 98.1 |  | 98.2 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.5 | 4.5 | 2 | http://powerquality.eaton.com/Products-services/ |  | Other | Other |  | No |  | http://powerquality.eaton.com/Products-services/ | N/A | 2011-08-01 | 2013-11-15 | United States, Japan, Canada | ES_29597_EATON 3S750_11152013151803_4764879
2194421 | Eaton Corporation | EATON | EATON 3S550 | EATON 3S550 |  | Ac-output UPS | Static | EATON 3S550 | 330 | 550 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | No |  | 86 | 140 | 335 | 10 | 1 | 0 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 10.1 |  | 94.8 |  | 97.3 |  | 97.9 |  | 98.2 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.5 | 4.5 | 2 | http://powerquality.eaton.com/Products-services/ |  | Other | Other |  | No |  | http://powerquality.eaton.com/Products-services/ | N/A | 2011-08-01 | 2013-11-15 | United States, Japan, Canada | ES_29597_EATON 3S550_11152013152411_6159982
2197654 | Eaton Corporation | EATON | 5P1500, 5P1500R | 5P1500, 5P1500R |  | Ac-output UPS | Static | 5P1500 | 1100 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 1 | 233 | 445 | 335 | 8 | 3 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 16.7 |  | 93.8 |  | 96.3 |  | 96.8 |  | 97 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 8 | 2 | http://powerquality.eaton.com/Products-services/ |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/ | N/A | 2013-08-01 | 2013-12-03 | United States, Japan, Canada | ES_29597_5P1500, 5P1500R_12032013144616_8902148
2216497 | Eaton Corporation | EATON | Power Xpert | 9395-275 |  | Ac-output UPS | Static | 9395-275 | 250000 | 275000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Data Center | 400-480 | 50-60 | 400-480 | 50-60 | No |  | 1877 | 1341 | 874 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 5132 | 523 | 90.9 | 97.7 | 93.6 | 99.3 | 94.3 | 99.3 | 94.5 | 99.4 | 93.1 | 98.9 | [7 empty] | 0.99 | 1 | [21 empty] | 93.1 | 9395-275 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.7 | 17.2 | 1 yr | http://powerquality.eaton.com/Products-services/Services/Battery-Services.asp |  | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,Modbus RTU | CAN Bridge, SNMP (v1/3) | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2007-07-20 | 2014-07-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395-275_07292014130242_8962139
2218436 | Eaton Corporation | EATON | BladeUPS 12 | BladeUPS 12 |  | Ac-output UPS | Static | BladeUPS 12 | 12000 | 12000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Data Center | 120-208 | 50-60 | 120-208 | 50-60 | Yes |  | 261 | 441 | 660 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 458.53 | 145.3 | 84.3 | 95 | 88.9 | 96.4 | 89.7 | 96.6 | 0 | 96.5 | 88 | 96 | [7 empty] | 0.99 | 0.99 | [21 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),HTTP |  | Yes | www.eaton.com/powerquality | www.eaton.com/powerquality | N/A | 2006-11-28 | 2014-08-28 | United States | ES_29597_BladeUPS 12_08292014125837_4071194
2241375 | Eaton Corporation | EATON | 93PM Series | 93PM-200-* |  | Ac-output UPS | Static | 93PM-200-1 | 20000 | 20000 | 93PM-200-4 | 200000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 813 | 1068 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 642 | 229 | 88.4 | 95.6 | 93.4 | 97.6 | 95 | 98.3 | 95.8 | 98.6 | 92.5 | 97.2 | [7 empty] | 0.98 | 0.77 | 2034 | 619 | 95.3 | 98.6 | 96.7 | 99 | 96.9 | 99.2 | 96.8 | 99.2 | 96.3 | 98.9 | [7 empty] | 1 | 1 | 92.5 | 730-D0057 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 3.1 | 8.8 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,HTTPS,HTTP,Modbus RTU | SNMP (v1orv2),BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/93PM.aspx?cx=3&GUID=DCE6372C-D9CB-4B99-96DD-43EBB6603A96 | N/A | 2013-11-23 | 2016-03-31 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_93PM-200-*_06092015211501_4501025
2241376 | Eaton Corporation | EATON | 93PM Series | 93PM-150-* |  | Ac-output UPS | Static | 93PM-150-1 | 20000 | 20000 | 93PM-150-3 | 150000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 560 | 1068 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 613 | 348 | 88.8 | 95.9 | 93.5 | 97.8 | 95.1 | 98.4 | 95.9 | 98.7 | 92.7 | 97.4 | [7 empty] | 0.99 | 0.78 | 1554 | 468 | 95.2 | 98.5 | 96.6 | 99.1 | 96.8 | 99.2 | 96.7 | 99.2 | 96.2 | 98.9 | [7 empty] | 1 | 1 | 92.7 | 730-D0057 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 4.2 | 13.4 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,HTTPS,HTTP,Modbus RTU | SNMP (v1 or 2),BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/93PM.aspx?cx=3&GUID=DCE6372C-D9CB-4B99-96DD-43EBB6603A96 | N/A | 2013-11-23 | 2016-03-31 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_93PM-150-*_06102015154959_1399335
2241377 | Eaton Corporation | EATON | 93PM Series | 93PM-100-* |  | Ac-output UPS | Static | 93PM-100-1 | 20000 | 20000 | 93PM-100-2 | 100000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 560 | 1068 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 559 | 215 | 88.8 | 95.9 | 93.7 | 97.8 | 95.2 | 98.5 | 96 | 98.8 | 92.8 | 97.5 | [7 empty] | 0.98 | 0.77 | 1177 | 352 | 94.9 | 98.4 | 96.6 | 99 | 96.8 | 99.2 | 96.7 | 99.2 | 96.2 | 98.9 | [7 empty] | 1 | 1 | 92.8 | 730-D0057 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 20.5 | 47.4 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,HTTPS,HTTP,Modbus RTU | SNMP (v1 or 2),BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/93PM.aspx?cx=3&GUID=DCE6372C-D9CB-4B99-96DD-43EBB6603A96 | N/A | 2013-03-28 | 2016-03-31 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_93PM-100-*_06102015161029_2629319
2241378 | Eaton Corporation | EATON | 93PM Series | 93PM-50-* |  | Ac-output UPS | Static | 93PM-50-1 | 20000 | 20000 | 93PM-50-1 | 50000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 560 | 1068 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 518 | 205 | 90.6 | 96.5 | 94.5 | 98 | 95.8 | 98.6 | 96.4 | 98.8 | 93.8 | 97.7 | [7 empty] | 0.98 | 0.78 | 519 | 225 | 95.3 | 98.2 | 96.7 | 98.9 | 96.9 | 99.1 | 96.8 | 99.2 | 96.3 | 98.7 | [7 empty] | 1 | 1 | 93.8 | 730-D0057 | Battery | Valve Regulated Lead-acid Battery | Integral | Yes | 9.5 | 24.7 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,HTTPS,HTTP,Modbus RTU | SNMP (v1 or 2),BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/93PM.aspx?cx=3&GUID=DCE6372C-D9CB-4B99-96DD-43EBB6603A96 | N/A | 2014-05-06 | 2016-03-31 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_93PM-50-*_06102015162048_3248356
2251084 | Eaton Corporation | EATON | 93PM Series | 93PM-400-* |  | Ac-output UPS | Static | 93PM-400-2 | 100000 | 100000 | 93PM-400-8 | 400000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 1623 | 1068 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1230.6 | 456.1 | 94.3 | 98 | 96 | 98.8 | 96.5 | 99.1 | 96.5 | 99.2 | 95.6 | 98.6 | [7 empty] | 0.99 | 0.96 | 3491.6 | 1241.6 | 95.5 | 98.5 | 96.6 | 99 | 96.7 | 99.1 | 96.6 | 99.1 | 96.3 | 98.8 | [7 empty] | 0.99 | 0.99 | 95.6 | 730-B1045 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 3.1 | 8.8 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/93PM.aspx?cx=3&GUID=DCE6372C-D9CB-4B99-96DD-43EBB6603A96 | N/A | 2013-11-23 | 2015-10-22 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_93PM-400-*_10222015132619_0379213
2255218 | Eaton Corporation | EATON | 9PX3K3U | 9PX3K3U |  | Ac-output UPS | Static | 9PX3K3U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 89 |  | 85.1 |  | 90.6 |  | 92.3 |  | 93.1 |  | 92.1 | [8 empty] | 0.99 | [22 empty] | 92.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 58 | 121 | 2 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | Other,SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2015-12-22 | 2015-12-18 | United States, Europe | ES_29597_9PX3K3U_12212015053808_4242757
2261743 | Eaton Corporation | EATON | 9PX2200IRT2U, 9PX2200IRT3U, 9PX2200GRT | 9PX2200IRT2U, 9PX2200IRT3U, 9PX2200GRT |  | Ac-output UPS | Static | 9PX2200IRT2U | 2200 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 48 |  | 89.3 |  | 92.5 |  | 93.3 |  | 93.3 |  | 93.1 | [8 empty] | 0.99 | [22 empty] | 93.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 60 | 120 | 3 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2016-03-08 | 2016-03-07 | United States, Europe | ES_29597_9PX2200IRT2U, 9PX2200IRT3U, 9PX2200GRT_03072016030900_8582453
2266340 | Eaton Corporation | EATON | Power Expert | 9395P-900 |  | Ac-output UPS | Static | 9395P-900 | 450000 | 450000 | 9395P-900 | 900000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 3581 | 892 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 4337.36 | 1046.42 | 95.4 | 98.8 | 96.7 | 99.2 | 96.8 | 99.3 | 96.8 | 99.3 | 96.3 | 99.1 | [7 empty] | 1 | 1 | 5918.08 | 1353.66 | 96.2 | 99.1 | 96.9 | 99.3 | 96.7 | 99.3 | 96.5 | 99.3 | 96.6 | 99.2 | [7 empty] | 1 | 1 | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 2.3 | 8.8 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1 or v2) | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2015-09-21 | 2016-05-10 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395P-900_05102016115222_1142499
2266341 | Eaton Corporation | EATON | Power Expert | 9395P-1200 |  | Ac-output UPS | Static | 9395P-1200 | 675000 | 675000 | 9395P-1200 | 1200000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1880 | 4321 | 892 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 6226.48 | 1349.63 | 95.5 | 98.9 | 96.7 | 99.3 | 96.8 | 99.4 | 96.8 | 99.4 | 96.4 | 99.2 | [7 empty] | 1 | 1 | 8155.56 | 1658.89 | 96.2 | 99.1 | 96.9 | 99.4 | 96.7 | 99.4 | 96.5 | 99.3 | 96.6 | 99.3 | [7 empty] | 1 | 1 | 96.4 | FI-UPM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 2.7 | 10.5 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1 or v2) | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2015-09-21 | 2016-05-10 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395P-1200_05102016115738_1458305
2267555 | Eaton Corporation | EATON | 9PX3000RT | 9PX3000RT |  | Ac-output UPS | Static | 9PX3000RT | 2700 | 3000 |  | 2700 |  | Other | ac - Other | Commercial,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.21 |  | 90.5 |  | 92.5 |  | 92.5 |  | 91.9 |  | 92.3 | [8 empty] | 0.99 | [22 empty] | 92.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3),HTTP |  | Yes | http://powerquality.eaton.com/Products-services/ | http://powerquality.eaton.com/Products-services/ | N/A | 2016-05-01 | 2016-05-19 | United States, Canada | ES_29597_9PX3000RT_05202016131043_4058972
2267556 | Eaton Corporation | EATON | 9PX2000RT | 9PX2000RT |  | Ac-output UPS | Static | 9PX2000RT | 1800 | 2000 |  | 1800 |  | Other | ac - Other | Commercial,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 41.44 |  | 88.1 |  | 91 |  | 91.1 |  | 95.9 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3),HTTP |  | Yes | http://powerquality.eaton.com/Products-services/ | http://powerquality.eaton.com/Products-services/ | N/A | 2016-05-01 | 2016-05-19 | United States, Canada | ES_29597_9PX2000RT_05202016131643_1885955
2272435 | Eaton Corporation | EATON | 9PX1000IRT, 9PX1000GRT | 9PX1000IRT, 9PX1000GRT | 9PX1000IRT2U,9PX1000IRT2U, | Ac-output UPS | Static | 9PX1000GRT | 1000 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 450 | 87 | 440 | 8 | 8 | 0 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 230 | 50 | 230 | 50 | 35 |  | 84.8 |  | 89.8 |  | 91.3 |  | 91.7 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 60 | 120 | 3 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | Other,SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2016-09-08 | 2016-09-12 | United States | ES_29597_9PX1000IRT, 9PX1000GRT_07152016062631_5061776
2272436 | Eaton Corporation | EATON | 9PX1500IRT, 9PX1500GRT | 9PX1500IRT, 9PX1500GRT | 9PX1500IRT2U,9PX1500IRT2U,; 9PX1500IRT2UANZ,9PX1500IRT2UANZ,; 9PX1500IRTM,9PX1500IRTM, | Ac-output UPS | Static | 9PX1500GRT | 1500 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 450 | 87 | 440 | 8 | 8 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 50.6 |  | 86.1 |  | 90.7 |  | 92 |  | 92.3 |  | 91.7 | [8 empty] | 0.99 | [22 empty] | 91.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 60 | 120 | 3 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | None | Other,SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2016-09-08 | 2016-09-12 | United States | ES_29597_9PX1500IRT, 9PX1500GRT_07152016074623_8629781
2274332 | Eaton Corporation | EATON | Power Xpert 9395 | 9395P-300 |  | Ac-output UPS | Static | 9395P-300 | 200000 | 200000 | 9395P-300 | 300000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1877 | 1341 | 874 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 2035 | 487 | 95.2 | 98.8 | 96.6 | 99.2 | 96.9 | 99.3 | 96.8 | 99.4 | 96.3 | 99.1 | [7 empty] | 1 | 0.99 | 2053 | 486 | 96.3 | 99.1 | 96.9 | 99.3 | 96.6 | 99.4 | 96.4 | 99.4 | 96.6 | 99.2 | [7 empty] | 1 | 1 | 96.3 | FI-UPM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 20.6 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS SNMP (v1 or v2) BAC | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2016-06-15 | 2016-08-05 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395P-300_08052016214258_3378846
2274333 | Eaton Corporation | EATON | Power Xpert 9395 | 9395P-600 |  | Ac-output UPS | Static | 9395P-600 | 400000 | 400000 | 9395P-600 | 600000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1877 | 1869 | 874 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 3490 | 852 | 95.7 | 98.9 | 96.9 | 99.3 | 97.1 | 99.4 | 97 | 99.4 | 96.6 | 99.1 | [7 empty] | 1 | 0.99 | 3493 | 854 | 96.5 | 99.1 | 97.1 | 99.4 | 96.8 | 99.4 | 96.6 | 99.4 | 96.8 | 99.3 | [7 empty] | 1 | 1 | 96.6 | FI-UPM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 2.8 | 5 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS SNMP (v1 or v2) BAC | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2016-06-15 | 2016-08-05 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395P-600_08052016214416_3456723
2281392 | Eaton Corporation | EATON | Power Expert | 9395P-1200 |  | Ac-output UPS | Static | 9395P-1200 | 675000 | 675000 | 9395P-1200 | 1100000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-600 | 50-60 | 380-600 | 50-60 | No |  | 1880 | 5655 | 892 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 600 | 60 | 600 | 60 | 10528 | 6027 | 94.4 | 97.9 | 96 | 98.8 | 96.1 | 99.1 | 95.9 | 99.2 | 95.6 | 98.6 | [7 empty] | 1 | 1 | 12184 | 6426 | 95.4 | 98.5 | 96.2 | 99.1 | 95.9 | 99.2 | 95.3 | 99.3 | 95.9 | 98.9 | [7 empty] | 1 | 1 | 95.6 | FI-UPM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 2.7 | 10.5 | 1 | N/A |  | Serial Port,Other,USB Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPSSNMP(v1,v2)BACnet/IP | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9395.aspx?cx=3 | N/A | 2016-01-29 | 2016-10-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9395P-1200_10132016212305_3785426
2292213 | Eaton Corporation | EATON | 9PX3000IRT2U, 9PX3000IRT3U, 9PX3000GRT, 9PX3000GLRT | 9PX3000IRT2U, 9PX3000IRT3U, 9PX3000GRT, 9PX3000GLRT | 9PX3000IRT2UANZ,9PX3000IRT2UANZ,; 9PX3000IRT3UANZ,9PX3000IRT3UANZ,; 9PX3000IRTM,9PX3000IRTM, | Ac-output UPS | Static | 9PX3000IRT2U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 54 |  | 89.4 |  | 92.5 |  | 93 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 60 | 120 | 3 | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 |  | Other | SNMP (v1, 2 or 3) |  | No |  | http://powerquality.eaton.com/Products-services/Backup-Power-UPS/9PX.aspx?cx=3 | N/A | 2016-03-05 | 2016-03-04 | United States, Europe | ES_29597_9PX3000IRT2U, 9PX3000IRT3U, 9PX3000GRT, 9PX3000GLRT_03042016062935_9425664
2331031 | Eaton Corporation | EATON | 9PX3000RTAU | 9PX3000RTAU |  | Ac-output UPS | Static | 9PX3000RTAU | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.4621 |  | 90.5 |  | 93.4 |  | 94.1 |  | 94.1 |  | 93.9 | [8 empty] | 0.99 | [22 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX3000RT.html | N/A | 2018-11-28 | 2018-11-28 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3000RTAU_11282018091941_5475913
2331032 | Eaton Corporation | EATON | 9PX2000RTAU | 9PX2000RTAU |  | Ac-output UPS | Static | 9PX2000RTAU | 1800 | 2000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.4783 |  | 88 |  | 92 |  | 93.1 |  | 93.3 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8 | 20 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX2000RT.html | N/A | 2018-11-28 | 2018-11-28 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX2000RTAU_11282018101449_2664488
2331033 | Eaton Corporation | EATON | 9PX1000IRT | 9PX1000IRT |  | Ac-output UPS | Static | 9PX1000IRT | 1000 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 450 | 440 | 8 | 8 |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.35 |  | 84.8 |  | 89.8 |  | 91.3 |  | 91.7 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX1000RT.html | N/A | 2018-12-05 | 2018-12-05 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX1000IRT_12052018153450_9804760
2331034 | Eaton Corporation | EATON | 9PX1000GRT | 9PX1000GRT |  | Ac-output UPS | Static | 9PX1000GRT | 1000 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 450 | 440 | 8 | 8 |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.35 |  | 84.8 |  | 89.8 |  | 91.3 |  | 91.7 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 17 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX1000GRT.html | N/A | 2018-12-05 | 2018-12-05 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX1000GRT_12052018155254_5587226
2331035 | Eaton Corporation | EATON | 9PX2200IRT2U | 9PX2200IRT2U |  | Ac-output UPS | Static | 9PX2200IRT2U | 2200 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.48 |  | 89.3 |  | 92.5 |  | 93.3 |  | 93.3 |  | 93.1 | [8 empty] | 0.99 | [22 empty] | 93.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/fr/en-gb/skuPage.9PX2200IRT2U.html | N/A | 2018-12-05 | 2018-12-05 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX2200IRT2U_12052018160306_1109988
2331036 | Eaton Corporation | EATON | 9PX2200IRT3U | 9PX2200IRT3U |  | Ac-output UPS | Static | 9PX2200IRT2U | 2200 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.48 |  | 89.3 |  | 92.5 |  | 93.3 |  | 93.3 |  | 93.1 | [8 empty] | 0.99 | [22 empty] | 93.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/fr/en-gb/skuPage.9PX2200IRT3U.html | N/A | 2018-12-05 | 2018-12-05 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX2200IRT3U_12052018161433_4837148
2331037 | Eaton Corporation | EATON | 9PX2200GRT | 9PX2200GRT |  | Ac-output UPS | Static | 9PX2200IRT2U | 2200 | 2200 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.48 |  | 89.3 |  | 92.5 |  | 93.3 |  | 93.3 |  | 93.1 | [8 empty] | 0.99 | [22 empty] | 93.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 17 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX2200GRT.html | N/A | 2018-12-05 | 2018-12-05 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX2200GRT_12052018161803_3909785
2331038 | Eaton Corporation | EATON | 9PX1500IRT | 9PX1500IRT |  | Ac-output UPS | Static | 9PX1500IRT | 1500 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 450 | 440 | 8 | 8 |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.506 |  | 86.1 |  | 90.7 |  | 92 |  | 92.3 |  | 91.7 | [8 empty] | 0.99 | [22 empty] | 91.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX1500RT.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX1500IRT_12062018100805_4054222
2331039 | Eaton Corporation | EATON | 9PX1500GRT | 9PX1500GRT |  | Ac-output UPS | Static | 9PX1500IRT | 1500 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 450 | 440 | 8 | 8 |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.506 |  | 86.1 |  | 90.7 |  | 92 |  | 92.3 |  | 91.7 | [8 empty] | 0.99 | [22 empty] | 91.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX1500GRT.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX1500GRT_12062018101917_6402276
2331040 | Eaton Corporation | EATON | 9PX3000IRT2U | 9PX3000IRT2U |  | Ac-output UPS | Static | 9PX3000IRT2U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.54 |  | 89.4 |  | 92.5 |  | 93 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/fr/en-gb/skuPage.9PX3000IRT2U.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_12062018112513_8919444
2331041 | Eaton Corporation | EATON | 9PX3000IRT3U | 9PX3000IRT3U |  | Ac-output UPS | Static | 9PX3000IRT2U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.54 |  | 89.4 |  | 92.5 |  | 93 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/fr/en-gb/skuPage.9PX3000IRT3U.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3000IRT3U_12062018113600_6216724
2331042 | Eaton Corporation | EATON | 9PX3000GRT | 9PX3000GRT |  | Ac-output UPS | Static | 9PX3000IRT2U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.54 |  | 89.4 |  | 92.5 |  | 93 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX3000GRT.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3000GRT_12062018113809_6167933
2331043 | Eaton Corporation | EATON | 9PX3000GLRT | 9PX3000GLRT |  | Ac-output UPS | Static | 9PX3000IRT2U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.54 |  | 89.4 |  | 92.5 |  | 93 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX3000GLRT.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3000GLRT_12062018114056_1919536
2331044 | Eaton Corporation | EATON | 9SX8KiPM | 9SX8KiPM |  | Ac-output UPS | Static | 9PX8KiPM | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.9984 |  | 92.4 |  | 94.4 |  | 94.7 |  | 94.6 |  | 94.6 | [8 empty] | 0.99 | [22 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://powerquality.eaton.com/dotnetpages/SKUPageMobile.aspx?productID=3425&cx=63 | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9SX8KiPM_12062018161015_3553788
2331045 | Eaton Corporation | EATON | 9PX8KPM | 9PX8KPM |  | Ac-output UPS | Static | 9PX8KiPM | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.9984 |  | 92.4 |  | 94.4 |  | 94.7 |  | 94.6 |  | 94.6 | [8 empty] | 0.99 | [22 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX8KPM.html | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX8KPM_12062018161214_6941087
2331046 | Eaton Corporation | EATON | 9PX8KiPM | 9PX8KiPM |  | Ac-output UPS | Static | 9PX8KiPM | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.9984 |  | 92.4 |  | 94.4 |  | 94.7 |  | 94.6 |  | 94.6 | [8 empty] | 0.99 | [22 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 16 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/dotnetpages/SKUPageMobile.aspx?mobile=true&cx=22&lx=11&productID=3450 | N/A | 2018-12-06 | 2018-12-06 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_Eaton Corporation_9PX8KiPM_12062018155651_4464524
2331275 | Eaton Corporation | EATON | 9PX11KPM | 9PX11KPM |  | Ac-output UPS | Static | 9PX11KiPM | 10000 | 11000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 1.07 |  | 93.6 |  | 94.8 |  | 95 |  | 94.8 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX11KPM.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX11KPM_12112018170829_8851735
2331276 | Eaton Corporation | EATON | 9SX11KiPM | 9SX11KiPM |  | Ac-output UPS | Static | 9PX11KiPM | 10000 | 11000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 1.07 |  | 93.6 |  | 94.8 |  | 95 |  | 94.8 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,HTTP |  | No |  | http://powerquality.eaton.com/dotnetpages/SKUPageMobile.aspx?productID=3427&cx=86 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9SX11KiPM_12112018170656_2556463
2331277 | Eaton Corporation | EATON | 9PX11KiPM | 9PX11KiPM |  | Ac-output UPS | Static | 9PX11KiPM | 10000 | 11000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-250 | 50-60 | 200-250 | 50-60 | Yes | 3 | 130 | 440 | 700 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 1.07 |  | 93.6 |  | 94.8 |  | 95 |  | 94.8 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 10 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/9PX11KiPM.aspx?cx=21 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES__9PX11KiPM_12112018165927_5794936
2331278 | Eaton Corporation | EATON | 9PX6Ki | 9PX6Ki |  | Ac-output UPS | Static | 9SX6KiRT | 5400 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.94 |  | 90.3 |  | 93.2 |  | 93.8 |  | 93.8 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/9PX6Ki.aspx | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX6Ki_12112018165611_8611786
2331279 | Eaton Corporation | EATON | 9PX6K | 9PX6K |  | Ac-output UPS | Static | 9SX6KiRT | 5400 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.94 |  | 90.3 |  | 93.2 |  | 93.8 |  | 93.8 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX6K.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX6K_12112018165458_6339178
2331280 | Eaton Corporation | EATON | 9SX6KiRT | 9SX6KiRT |  | Ac-output UPS | Static | 9SX6KiRT | 5400 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.94 |  | 90.3 |  | 93.2 |  | 93.8 |  | 93.8 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/9SX6KiRT.aspx | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9SX6KiRT_12112018164853_9804623
2331281 | Eaton Corporation | EATON | 9PX5Ki | 9PX5Ki |  | Ac-output UPS | Static | 9PX5K | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.89 |  | 87.1 |  | 91.8 |  | 93.2 |  | 93.6 |  | 92.9 | [8 empty] | 0.99 | [22 empty] | 92.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX5K.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX5Ki_12112018162442_7888359
2331282 | Eaton Corporation | EATON | 9SX5KiRT | 9SX5KiRT |  | Ac-output UPS | Static | 9PX5K | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.89 |  | 87.1 |  | 91.8 |  | 93.2 |  | 93.6 |  | 92.9 | [8 empty] | 0.99 | [22 empty] | 92.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/9SX5KiRT.aspx?cx=22 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9SX5KiRT_12112018162246_6509417
2331283 | Eaton Corporation | EATON | 9PX5K | 9PX5K |  | Ac-output UPS | Static | 9PX5K | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 0.89 |  | 87.1 |  | 91.8 |  | 93.2 |  | 93.6 |  | 92.9 | [8 empty] | 0.99 | [22 empty] | 92.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 8 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX5K.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX5K_12112018161439_1794832
2331284 | Eaton Corporation | EATON | 5PX3000iRTN | 5PX3000iRTN |  | Ac-output UPS | Static | 5PX3000iRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 86 | 441 | 647 | 9 |  |  | Voltage Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.214 |  | 96.9 |  | 98.1 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.5PX3000IRTN.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_5PX3000iRTN_12112018160017_2545765
2331285 | Eaton Corporation | EATON | 5PX3000iRT3UAU | 5PX3000iRT3UAU |  | Ac-output UPS | Static | 5PX3000iRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 131 | 441 | 497 | 9 |  |  | Voltage Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.214 |  | 96.9 |  | 98.1 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/5PX3000iRT3UAU.aspx?cx=22 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_5PX3000iRT3UAU_12112018155802_9192771
2331286 | Eaton Corporation | EATON | 5PX3000iRT3U | 5PX3000iRT3U |  | Ac-output UPS | Static | 5PX3000iRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 131 | 441 | 497 | 9 |  |  | Voltage Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.214 |  | 96.9 |  | 98.1 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/5PX3000iRT3U.aspx?cx=181&GUID=69A3813B-1F23-41DB-82F6-9150F9E54BB8 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_5PX3000iRT3U_12112018155528_6430103
2331287 | Eaton Corporation | EATON | 5PX3000iRT2UAU | 5PX3000iRT2UAU |  | Ac-output UPS | Static | 5PX3000iRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 86 | 441 | 647 | 9 |  |  | Voltage Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.214 |  | 96.9 |  | 98.1 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://powerquality.eaton.com/5PX3000iRT2UAU.aspx?cx=22 | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_5PX3000iRT2UAU_12112018155345_3564044
2331288 | Eaton Corporation | EATON | 5PX3000iRT2U | 5PX3000iRT2U |  | Ac-output UPS | Static | 5PX3000iRT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 86 | 441 | 647 | 9 |  |  | Voltage Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.214 |  | 96.9 |  | 98.1 |  | 98.5 |  | 98.6 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.5PX3000IRT2U.html | N/A | 2018-12-11 | 2018-12-11 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_5PX3000iRT2U_12112018154144_3963107
2331436 | Eaton Corporation | EATON | 9PX3K3U | 9PX3K3U |  | Ac-output UPS | Static | 9PX3K3U | 3000 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 3 | 130 | 440 | 722 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 50 | 230 | 50 | 0.89 |  | 85.2 |  | 90.7 |  | 92.4 |  | 93.1 |  | 92.1 | [8 empty] | 0.99 | [22 empty] | 92.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 18 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX3K3UNP2.html | N/A | 2018-11-28 | 2018-12-14 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3K3U_12142018082818_7653040
2331676 | Eaton Corporation | EATON | 9PX3000RT | 9PX3000RT |  | Ac-output UPS | Static | 9PX3000RT | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.4621 |  | 90.5 |  | 92.5 |  | 92.5 |  | 91.9 |  | 92.3 | [8 empty] | 0.99 | [22 empty] | 92.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 14 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX3000RT.html | N/A | 2018-11-28 | 2018-12-19 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX3000RT_12192018083920_7402461
2331677 | Eaton Corporation | EATON | 9PX2000RT | 9PX2000RT |  | Ac-output UPS | Static | 9PX2000RT | 1800 | 2000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 87 | 440 | 605 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.4144 |  | 88.1 |  | 91 |  | 91.1 |  | 95.9 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8 | 20 | 2 | N/A |  | Serial Port,USB Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.eaton.com/us/en-us/skuPage.9PX2000RT.html | N/A | 2018-11-28 | 2018-12-19 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_29597_9PX2000RT_12192018084606_2669490
2072786 | Eltek, Inc. | ELTEK | FLATPACK2 48/3000 HE | 241119.105 |  | Dc-output UPS | Static | FLATPACK2 48/3000 HE | 3000 | 3000 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 100-277 | 45-66 | 42-56 | - | No |  | 42 | 109 | 327 |  |  |  |  | No |  |  | 277 | 60 | 53 | [13 empty] | 11.5 | 96 | 97 | 97 | 96 | 96 | 96 | 0.98 | [22 empty] | 96.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239585&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_241119.105_10192012172200_3140836
2072787 | Eltek, Inc. | ELTEK | FLATPACK2 48/2000 HE | 241115.105 |  | Dc-output UPS | Static | FLATPACK2 48/2000 HE | 2000 | 2000 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 100-277 | 45-66 | 42-56 | - | No |  | 42 | 109 | 327 |  |  |  |  | No |  |  | 277 | 60 | 53 | [13 empty] | 11.5 | 96 | 97 | 97 | 96 | 96 | 96 | 0.98 | [22 empty] | 96.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239585&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_241115.105_10192012172256_7239421
2072788 | Eltek, Inc. | ELTEK | FLATPACK2 48-60/2000 HE | 241115.705 |  | Dc-output UPS | Static | FLATPACK2 48-60/2000 HE | 2000 | 2000 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 100-277 | 45-66 | 42-56 | - | No |  | 42 | 109 | 327 |  |  |  |  | No |  |  | 277 | 60 | 53 | [13 empty] | 11.5 | 96 | 97 | 97 | 96 | 96 | 96 | 0.98 | [22 empty] | 96.4 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239585&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_241115.705_10192012172406_3282981
2072789 | Eltek, Inc. | ELTEK | V2000A1-HE | V2000A1-HE |  | Dc-output UPS | Static | V2000A1-HE | 2000 | 2000 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 200-240 | 50-60 | 42-56 | - | No |  | 88 | 86 | 280 |  |  |  |  | No |  |  | 240 | 60 | 53 | [13 empty] | 18.8 | 96.3 | 96.6 | 96.3 | 96.1 | 96.5 | 95.7 | 0.94 | [22 empty] | 96.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239575&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_V2000A1-HE_10192012175207_8738195
2072790 | Eltek, Inc. | ELTEK | V1500A1-HE | V1500A1-HE |  | Dc-output UPS | Static | V1500A1-HE | 1500 | 1500 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 200-240 | 50-60 | 42-56 | - | No |  | 88 | 86 | 280 |  |  |  |  | No |  |  | 240 | 60 | 53 | [13 empty] | 18.8 | 96.3 | 96.6 | 96.3 | 96.1 | 96.5 | 95.7 | 0.94 | [22 empty] | 96.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239575&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_V1500A1-HE_10192012175428_7762303
2072791 | Eltek, Inc. | ELTEK | V1000A1-HE | V1000A1-HE |  | Dc-output UPS | Static | V1000A1-HE | 1000 | 1000 |  |  |  |  | Direct Current (dc) | Commercial,Data Center,Telecommunications | 200-240 | 50-60 | 42-56 | - | No |  | 88 | 86 | 280 |  |  |  |  | No |  |  | 240 | 60 | 53 | [13 empty] | 18.8 | 96.3 | 96.6 | 96.3 | 96.1 | 96.5 | 95.7 | 0.94 | [22 empty] | 96.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | http://www.eltek.com/us/wip4/detail_products.epl?id=1239575&cat=&k1=&k2=&k3=&k4=&close=1 | N/A | 2012-10-01 | 2012-10-17 | United States | ES_1107363_V1000A1-HE_10192012175750_1554693
2244372 | Eltek, Inc. | FLATPACK2 380/3000 HE | FLATPACK2 380/3000 HE | 241119.825 |  | Dc-output UPS | Static | FLATPACK2 380/3000 HE | 3000 | 3000 |  |  |  |  | Direct Current (dc) | Data Center,Telecommunications | 100-277 | 50-60 | 380-381 | - | Yes | 1 | 43 | 110 | 335 |  |  |  |  | No |  |  | 277 | 60 | 381 | [13 empty] | 15.076 | 99.8 | 99 | 98.6 | 98.2 | 97.5 | 96.8 | 0.99 | [22 empty] | 98.3 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | www.eltek.com | N/A | 2014-11-01 | 2015-07-10 | United States, Europe | ES_1107363_241119.825_07232015074706_8902495
2212203 | Eltek, Inc. | FlatPack S 48/1800 HE Rectifier,FlatPack S 48/1000 HE Rectifier | FlatPack S 48V HE Rectifier Series | 241122.125 | FlatPack S 48V HE Rectifier Series,241122.105, | Dc-output UPS | Static | FlatPack S 48/1800 HE Rectifier | 1800 | 1800 |  |  |  |  | Direct Current (dc) | Telecommunications | 100-250 | 50-60 | 53-54 | - | Yes | 1 | 44 | 3 | 8 |  |  |  |  | No |  |  | 230 | 60 | 53 | [13 empty] | 11.3916 | 96 | 96.1 | 95.9 | 95.6 | 95.4 | 94.8 | 0.96 | [22 empty] | 95.6 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | None | None |  | No |  | WWW.ELTEK.COM | N/A | 2012-10-01 | 2014-04-24 | United States, Europe | ES_1107363_241122.125_06022014135224_9627696
2245441 | Fuji Electric Corp. of America | Fuji Electric | UPS7000HX-T3U/500 | UPS7000HX-T3U/500 |  | Ac-output UPS | Static | UPS7000HX-T3U/500 | 500000 | 500000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 384-528 | 57-63 | 480-480 | 60-60 | No |  | 2000 | 2000 | 900 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 4130 |  | 96.1 |  | 97.2 |  | 97.3 |  | 97.2 |  | 97 | [8 empty] | 0.99 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | N/A | N/A | N/A | N/A | N/A |  | Serial Port | SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.americas.fujielectric.com/systems/ups/ups7000hx-t3u | N/A | 2015-07-08 | 2015-07-08 | United States, Canada | ES_1024117_UPS7000HX-T3U500_08072015092327_1499295
2282481 | Fuji Electric Corp. of America | Fuji Electric | UPS7300WX-T3U/225 | UPS7300WX-T3U/225 |  | Ac-output UPS | Static | 1 | 225000 | 225000 | N/A |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 432-528 | 54-66 | 480-480 | 59-61 | No |  | 2050 | 1500 | 900 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 2.5 | 2 | 95.3 | 96.4 | 96.9 | 98 | 97.3 | 98.5 | 97.4 | 98.8 | 96.6 | 97.7 | [7 empty] | 1 | 1 | [21 empty] | 96.6 | 1 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | N/A | N/A | N/A | N/A | N/A |  | Serial Port | SNMP (v1, 2 or 3),Modbus RTU |  | No |  | in preparation | N/A | 2016-11-01 | 2016-10-26 | United States, Canada | ES_1024117_UPS7300WX-T3U225_10262016151230_3759320
2282482 | Fuji Electric Corp. of America | Fuji Electric | UPS7300WX-T3U/300 | UPS7300WX-T3U/300 |  | Ac-output UPS | Static | 1 | 300000 | 300000 | N/A |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 432-528 | 54-66 | 480-480 | 59-61 | No |  | 2050 | 1500 | 900 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 2.5 | 2.1 | 96.1 | 97.1 | 97.2 | 98.4 | 97.4 | 98.8 | 97.4 | 98.9 | 97 | 98.2 | [7 empty] | 1 | 1 | [21 empty] | 97 | 1 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | N/A | N/A | N/A | N/A | N/A |  | Serial Port | SNMP (v1, 2 or 3),Modbus RTU |  | No |  | in preparation | N/A | 2016-11-01 | 2016-10-26 | United States, Canada | ES_1024117_UPS7300WX-T3U300_10262016152012_4680190
2282483 | Fuji Electric Corp. of America | Fuji Electric | UPS7300WX-T3U/333 | UPS7300WX-T3U/333 |  | Ac-output UPS | Static | 1 | 333000 | 333000 | N/A |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 432-528 | 54-66 | 480-480 | 59-61 | No |  | 2050 | 1500 | 900 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 2.5 | 1.8 | 96.4 | 97.4 | 97.3 | 98.5 | 97.4 | 98.9 | 97.4 | 99 | 97.1 | 98.3 | [7 empty] | 1 | 1 | [21 empty] | 97.1 | 1 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | N/A | N/A | N/A | N/A | N/A |  | Serial Port | SNMP (v1, 2 or 3),Modbus RTU |  | No |  | in preparation | N/A | 2016-11-01 | 2016-10-26 | United States, Canada | ES_1024117_UPS7300WX-T3U333_10262016152035_8632306
2192141 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-10KRTL | UPS2000-G-10KRTL |  | Ac-output UPS | Static | UPS2000-G-10KRTS | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes | 2 | 85 | 430 | 550 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 66 |  | 94.3 |  | 95.2 |  | 95.1 |  | 94.8 |  | 95 | [8 empty] | 1 | [22 empty] | 95 | N/A | Battery | N/A | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,Ethernet | HTTPS,SNMP (v1, 2 or 3),HTTP,Modbus RTU |  | Yes |  | http://www.huawei.com/cn/products/network-energy/ups/ups2000-g/index.htm | N/A | 2012-12-30 | 2013-09-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_HUAWEI TECHNOLOGIES CO LTD (159971) ¦ UPS2000-G-10KRTL_09302013144329_2209008
2192142 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-15KRTL | UPS2000-G-15KRTL |  | Ac-output UPS | Static | UPS2000-G-15KRTL | 13500 | 15000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes | 2 | 85 | 430 | 550 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 158.7 |  | 92.2 |  | 94 |  | 94.5 |  | 94.6 |  | 93.7 | [8 empty] | 1 | [22 empty] | 93.7 | N/A | Battery | N/A | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU |  | Yes |  | http://www.huawei.com/cn/products/network-energy/ups/ups2000-g/index.htm | N/A | 2012-12-30 | 2013-09-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_HUAWEI TECHNOLOGIES CO LTD (159971) ¦ UPS2000-G-15KRTL_09302013144102_2062184
2192143 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-20KRTL | UPS2000-G-20KRTL |  | Ac-output UPS | Static | UPS2000-G-20KRTL | 18000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes | 2 | 85 | 430 | 550 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 158.8 |  | 93.4 |  | 94.5 |  | 94.7 |  | 94.6 |  | 94.3 | [8 empty] | 1 | [22 empty] | 94.3 | N/A | Battery | N/A | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU |  | Yes |  | http://www.huawei.com/cn/products/network-energy/ups/ups2000-g/index.htm | N/A | 2012-12-30 | 2013-09-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_HUAWEI TECHNOLOGIES CO LTD (159971) ¦ UPS2000-G-20KRTL_09302013144201_2121879
2192144 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-6KRTL | UPS2000-G-6KRTL |  | Ac-output UPS | Static | UPS2000-G-6KRTS | 5400 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes | 2 | 85 | 430 | 550 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 54.55 |  | 93.3 |  | 94.3 |  | 94.4 |  | 94.1 |  | 94.3 | [8 empty] | 1 | [22 empty] | 94.3 | N/A | Battery | N/A | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU |  | Yes |  | http://www.huawei.com/cn/products/network-energy/ups/ups2000-g/index.htm | N/A | 2012-12-30 | 2013-09-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_HUAWEI TECHNOLOGIES CO LTD (159971) ¦ UPS2000-G-6KRTL_09302013143956_1996825
2294938 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-E-125K-BF | UPS5000-E-125K-BF |  | Ac-output UPS | Static | 5 | 125000 | 125000 | 5 |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | Yes | 5 | 2000 | 600 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 593.44 | 52.46 | 96 | 99.5 | 96.5 | 99.5 | 96.2 | 99.5 | 95.7 | 99.4 | 96.3 | 99.5 | [7 empty] | 1 | 1 | [21 empty] | 98.7 | 5 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by the customer | Determined by the customer | Decided by the customer | NA |  | Ethernet | Modbus TCP |  | Yes |  | http://3ms.huawei.com/mm/docMaintain/mmMaintain.do?method=showMMDetail&f_id=DCI16090810080444 | Determined by the customer | 2017-01-01 | 2017-04-26 | United States, Canada | ES_1100906_UPS5000-E-125K-BF_04242017152423_5665704
2294939 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-E-75K-BF | UPS5000-E-75K-BF |  | Ac-output UPS | Static | 3 | 75000 | 75000 | 3 |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | Yes | 3 | 2000 | 600 | 1100 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 404.1 | 254.84 | 95.8 | 98.4 | 96.5 | 99 | 96.2 | 99.1 | 95.8 | 99.2 | 96.3 | 98.9 | [7 empty] | 1 | 1 | [21 empty] | 97 | 3 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by the customer | Determined by the customer | Decided by the customer | NA |  | Ethernet | Modbus TCP |  | Yes |  | http://3ms.huawei.com/mm/docMaintain/mmMaintain.do?method=showMMDetail&f_id=DCI16090810080444 | Determined by the customer | 2017-01-01 | 2017-04-26 | United States, Canada | ES_1100906_UPS5000-E-75K-BF_04212017111101_8862420
2303096 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-E-125K-FM | UPS5000-E-125K-FM |  | Ac-output UPS | Static | 5 | 125000 | 125000 | 5 |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | Yes | 5 | 2000 | 600 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 593.44 | 52.46 | 96 | 99.5 | 96.5 | 99.5 | 96.2 | 99.5 | 95.7 | 99.4 | 96.3 | 99.5 | [7 empty] | 1 | 1 | [21 empty] | 98.7 | 5 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by the customer | Determined by the customer | Decided by the customer | NA |  | Ethernet | Modbus TCP |  | Yes |  | http://3ms.huawei.com/mm/docMaintain/mmMaintain.do?method=showMMDetail&f_id=DCI16090810080444 | Determined by the customer | 2017-01-01 | 2017-08-30 | United States, Canada | ES_1100906_UPS5000-E-125K-FM_08292017231629_1704980
2306326 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-S-300K-SM | UPS5000-S-300K-SM | ,UPS5000-S-300K-SMT,; ,UPS5000-S-500K-FM,; ,UPS5000-S-500K-SM, | Ac-output UPS | Static | UPS5000-S-300K-SM | 300000 | 300000 | UPS5000-S-500K-FM | 500000 |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | Yes | 5 | 2000 | 1200 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 1094.82 | 792.2 | 96.6 | 98.8 | 96.9 | 99.2 | 96.3 | 99.3 | 95.7 | 99.3 | 96.7 | 99.1 | [7 empty] | 1 | 1 | 1755.18 | 171.7 | 96.8 | 99.5 | 96.9 | 99.5 | 96.5 | 99.3 | 95.9 | 99.2 | 96.8 | 99.4 | [7 empty] | 1 | 1 | 97.3 | UPS5000-S-300K-SM;UPS5000-S-500K-FM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by the customer | Determined by the customer | Decided by the customer | NA |  | Ethernet | Modbus TCP |  | Yes |  | http://3ms.huawei.com/mm/docMaintain/mmMaintain.do?method=showMMDetail&f_id=DCI16090810080444 | Determined by the customer | 2017-11-08 | 2017-11-10 | United States, Canada | ES_1100906_UPS5000-S-300K-SM_11082017134806_8283044
2306327 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-E-300K-SM | UPS5000-E-300K-SM | ,UPS5000-E-300K-SMT,; ,UPS5000-E-500K-FM,; ,UPS5000-E-500K-SM, | Ac-output UPS | Static | UPS5000-E-300K-SM | 300000 | 300000 | UPS5000-E-500K-FM | 500000 |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | Yes | 5 | 2000 | 1200 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 1562.16 | 896.8 | 95.4 | 98.8 | 95.7 | 99.2 | 95.3 | 99.3 | 94.6 | 99.3 | 95.5 | 99.1 | [7 empty] | 1 | 1 | 2395.25 | 171.54 | 95.4 | 99.5 | 95.7 | 99.4 | 95.3 | 99.3 | 94.6 | 99.2 | 95.5 | 99.4 | [7 empty] | 1 | 1 | 96.4 | UPS5000-E-300K-SM;UPS5000-E-500K-FM | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by the customer | Determined by the customer | Decided by the customer | NA |  | Ethernet | Modbus TCP |  | Yes |  | http://3ms.huawei.com/mm/docMaintain/mmMaintain.do?method=showMMDetail&f_id=DCI16090810080444 | Determined by the customer | 2017-11-08 | 2017-11-10 | United States, Canada | ES_1100906_UPS5000-E-300K-SM_11082017145134_7597619
2331574 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-E-75K-BF | UPS5000-E-75K-BF | ,UPS5000-E-125K-FM, | Ac-output UPS | Static | UPS5000-E-75K-BF | 75000 | 75000 | UPS5000-E-125K-FM | 125000 |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 200 | 600 | 1100 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 355 | 240 | 95.6 | 98.5 | 95.9 | 98.9 | 95.5 | 99.1 | 94.6 | 99.2 | 95.7 | [8 empty] | 0.99 | 0.99 | 580 | 368 | 95.6 | 98.5 | 95.8 | 99 | 95.4 | 99.1 | 94.5 | 99.2 | 95.7 | [8 empty] | 0.99 | 0.99 | 95.7 | PM25K-V4S | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 30 | 30 | 5 | N/A |  | Ethernet | Modbus TCP |  | Yes |  | http://detail.zol.com.cn/ups/huawei/ | N/A | 2018-11-06 | 2018-12-06 | United States, Canada | ES_1100906_UPS5000-E-75K-BF_11082018102113_885431
2331575 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-6KRTL | UPS2000-G-6KRTL | ,UPS2000-G-10KRTL, | Ac-output UPS | Static | UPS2000-G-10KRTL | 9000 | 10000 |  |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 220-240 | 50-60 | No |  | 430 | 86 | 615 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 240 | 60 | 66 | 65 | 94.2 | 97.1 | 95.1 | 98.5 | 95.1 | 99 | 94.8 | 99 | 95 | [8 empty] | 0.96 | 1 | [21 empty] | 95 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 20 | 20 | 5 | N/A |  | Ethernet | Modbus TCP |  | Yes |  | http://detail.zol.com.cn/ups/index404866.shtml | N/A | 2018-11-06 | 2018-12-06 | United States, Canada | ES_1100906_UPS2000-G-6KRTL_11082018090647_2623102
2331576 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-A-6KTTL-S | UPS2000-A-6KTTL-S | ,UPS2000-A-10KTTL-S, | Ac-output UPS | Static | UPS2000-A-10KTTL-S | 9000 | 10000 |  |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 220-240 | 50-60 | 220-240 | 50-60 | No |  | 580 | 250 | 605 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 230 | 60 | 230 | 60 | 58 | 54 | 95.3 | 97.9 | 95.9 | 98.7 | 95.9 | 99 | 95.7 | 99 | 95.8 | 99 | [7 empty] | 0.99 | 1 | [21 empty] | 95.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 20 | 20 | 5 | N/A |  | Ethernet | Modbus TCP |  | Yes |  | https://item.jd.com/22763904157.html#crumb-wrap | N/A | 2018-11-06 | 2018-12-06 | United States, Canada | ES_1100906_UPS2000-A-6KTTL-S_11072018194242_7175714
2331577 | Huawei Technologies Co., Ltd. | HUAWEI | UPS5000-S-200K-FM | UPS5000-S-200K-FM | ,-500K-SM,; ,UPS5000-S,; ,UPS5000-S-200K-SM,; ,UPS5000-S-300K-SM,; ,UPS5000-S-300K-SMT,; ,UPS5000-S-400K-FM,; ,UPS5000-S-400K-SM,; ,UPS5000-S-500K-FM,; ,UPS5000-S-600K-FM,; ,UPS5000-S-600K-SM,; ,UPS5000-S-800K-FM,; ,UPS5000-S-800K-SM, | Ac-output UPS | Static | UPS5000-S-200K-FM | 200000 | 200000 | UPS5000-S-800K-FM | 800000 |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 2400 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 786.2 | 523.7 | 96.6 | 98.8 | 96.8 | 99.1 | 96.5 | 99.2 | 95.9 | 99.2 | 96.7 | [8 empty] | 0.99 | 1 | 2912 | 1812 | 96.6 | 98.8 | 96.8 | 99.1 | 96.4 | 99.2 | 96 | 99.2 | 96.7 | [8 empty] | 0.99 | 0.99 | 96.7 | PM50K-V4H | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 30 | 30 | 5 | N/A |  | Ethernet | Modbus TCP |  | Yes |  | http://detail.zol.com.cn/ups/huawei/ | N/A | 2018-11-15 | 2018-12-06 | United States, Canada | ES_1100906_UPS5000-S-200K-FM_11152018150358_2990686
2331602 | Huawei Technologies Co., Ltd. | HUAWEI | UPS2000-G-15KRTL | UPS2000-G-15KRTL | ,UPS2000-G-20KRTL, | Ac-output UPS | Static | UPS2000-G-20KRTL | 18000 | 20000 |  |  |  | Multi-Mode Line Interactive | ac - Other | Commercial | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 430 | 130 | 757 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 415 | 60 | 415 | 60 | 165.3 | 161 | 93.7 | 96.7 | 94.9 | 98.3 | 95 | 98.8 | 94.8 | 99 | 94.6 | [8 empty] | 0.99 | 1 | [21 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 20 | 20 | 5 | N/A |  | Ethernet | Modbus TCP |  | Yes |  | http://item.jd.com/21222937753.html?cu=true&utm_source=kong&utm_medium=cpc&utm_campaign=t_281_20170818001&utm_term=_0_2466b4044ed24d61b489dfd498f15dc3 | N/A | 2018-11-06 | 2018-12-13 | United States, Canada | ES_1100906_UPS2000-G-15KRTL_12132018091402_8293573
2282605 | Ingram Micro Inc. | Ingram Micro Inc. | UPS1RM2U1500-1N | UPS1RM2U1500-1N |  | Ac-output UPS | Static | UPS1RM2U1500-1N | 1296 | 1440 |  |  |  | Other | ac - Other | Consumer | 110-127 | 50-60 | 110-127 | 50-60 | Yes |  | 85 | 304 | 510 | 8 | 4 |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.462 |  | 96.2 |  | 97.2 |  | 97 |  | 96.8 |  | 97 | [8 empty] | 1 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 years | N/A |  | None | None |  | Yes |  | www.V7_world.com | N/A | 2016-10-15 | 2016-10-17 | United States, Canada | ES_1137292_UPS1RM2U1500-1N_10182016130854_4330884
2294043 | Ingram Micro Inc. | Ingram Micro Inc. | UPS1RM2U3000-1N | UPS1RM2U3000-1N |  | Ac-output UPS | Static | UPS1RM2U3000-1N | 2592 | 2880 |  |  |  | Other | ac - Other | Consumer | 110-127 | 50-60 | 110-127 | 50-60 | Yes | 2 | 88 | 438 | 600 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.6 |  | 95.5 |  | 97.1 |  | 97.1 |  | 97.3 |  | 97.2 | [8 empty] | 1 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 mins | 10 mins | 3 years | N/A |  | None | None |  | Yes |  | www.V7_world.com | N/A | 2017-03-15 | 2017-04-11 | United States, Canada | ES_1137292_UPS1RM2U3000-1N_04112017145847_5417843
2284894 | Ingram Micro Inc. | V7 | UPS1DT750-1N | UPS1DT750-1N |  | Ac-output UPS | Static | UPS1DT750-1N | 450 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 100 | 160 | 290 | 10 | 10 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.59 |  | 97.2 |  | 98.1 |  | 98 |  | 97.7 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.v7-world.com/us/products/network/ups-systems.html |  | USB Port | None |  | No |  | http://www.v7-world.com/us/products/network/ups-systems.html | N/A | 2016-11-28 | 2016-11-28 | United States | ES_1137292_UPS1DT750-1N_11232016213448_7654077
2284895 | Ingram Micro Inc. | V7 | UPS1DT550-1N | UPS1DT550-1N |  | Ac-output UPS | Static | UPS1DT550-1N | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 100 | 160 | 290 | 10 | 10 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.59 |  | 96.6 |  | 97.7 |  | 97.9 |  | 97.7 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.v7-world.com/us/products/network/ups-systems.html |  | USB Port | None |  | No |  | http://www.v7-world.com/us/products/network/ups-systems.html | N/A | 2016-11-28 | 2016-11-28 | United States | ES_1137292_UPS1DT550-1N_11232016212158_7697816
2300511 | Ingram Micro Inc. | V7 | UPS1TW1500-1N | UPS1TW1500-1N |  | Ac-output UPS | Static | UPS1TW1500-1N | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 101 | 406 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.85 |  | 94.6 |  | 96.5 |  | 97 |  | 96.9 |  | 96.8 | [8 empty] | 0.99 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.v7-world.com/us/products/network/ups-systems.html |  | USB Port | None |  | No |  | http://www.v7-world.com/us/products/network/ups-systems.html | N/A | 2017-08-01 | 2017-07-25 | United States, Canada | ES_1137292_UPS1TW1500-1N_07202017042653_2402575
2174043 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | 1100A Series | 1100A Series |  | Ac-output UPS | Static | UP1133A-A103SU-2 | 9000 | 10000 | UP1133A-A503SU | 45000 |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 120-208 | 54-66 | 120-208 | 60-63 | Yes | 28 | 1400 | 500 | 686 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 0 |  | 0 |  | 95.8 |  | 95.1 |  | 94.2 |  | 95 | [8 empty] | 0.9 |  | 0 |  | 92.1 |  | 93.5 |  | 92.6 |  | 0 |  | 92.9 | [8 empty] | 0.9 | 0.9 | 95 | PMAU-02 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 18-5 | 36-10 | 2 | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/1100.aspx |  | Serial Port | None |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/1100.aspx | None | 2013-02-01 | 2013-02-28 | United States | ES_1119276_1100A Series_02272013231151_9323541
2221278 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | 9900C Series | 9900C Series |  | Ac-output UPS | Static | UP9933C-A105DU-4 | 1000000 | 1050000 | UP9933C-B215DU-4 | 1995000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 384-552 | 54-66 | 494-466 | 60-60 | No |  | 2000 | 3003 | 900 | 0 | 0 | 0 | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 245600 |  | 96.4 |  | 97 |  | 96.9 |  | 96.7 |  | 96.8 | [8 empty] | 0.99 |  | 11035.09 |  | 95.9 |  | 96.7 |  | 96.6 |  | 96.6 |  | 96.5 | [8 empty] | 1 | 1 | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Variable | Variable | 36 months or 42 months | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/PeripheralBatteryCabinets.aspx |  | USB Port,Ethernet | Modbus TCP |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/9900C.aspx | None | 2014-05-01 | 2014-10-03 | United States | ES_1119276_9900C_10022014133311_4721795
2266856 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | Summit-500 | Summit-500 |  | Ac-output UPS | Static | UPSU33E-A504DU-4 | 500000 | 500000 | UPSU33E-A504DU-4 |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 384-552 | 54-66 | 466-494 | 60-60 | No |  | 2220 | 1680 | 1040 | 0 | 0 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 0 |  | 97.7 |  | 97.7 |  | 97.4 |  | 0 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | UPSU33E-A504DU-4 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Variable | Variable | 24 months or 30 months | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/PeripheralBatteryCabinets.aspx | NA | USB Port,Ethernet | Modbus TCP | NA | No | No | NA | None | 2016-04-29 | 2016-05-07 | United States | ES_1119276_Type UPSU33E-A504DU-4_04222016144319_2412378
2266857 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | 9900Aegis Series | 9900Aegis Series |  | Ac-output UPS | Static | UP9933A-E234DU-4 | 202500 | 225000 | UP9933A-E234DU-4 |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 384-552 | 54-66 | 432-528 | 60-60 | No |  | 222 | 108 | 102 | 0 | 0 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 0 |  | 96.2 |  | 96.9 |  | 97.5 |  | 0 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | UP9933A-E234DU-4 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Variable | Variable | 36 months or 42 months | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/PeripheralBatteryCabinets.aspx | N/A | Serial Port | Modbus TCP | N/A | No | No | N/A | None | 2016-04-29 | 2016-05-17 | United States | ES_1119276_Type UP9933A-E234DU-4_04232016202255_7460901
2305868 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | Summit-750 | Summit-750 |  | Ac-output UPS | Static | UPSU33E-A754DU-4 | 750000 | 750000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 384-552 | 54-66 | 466-494 | 60-60 | No |  | 2047 | 2073 | 858 | 0 | 0 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 2662.43 |  | 98.9 |  | 99.1 |  | 98.8 |  | 97.5 |  | 99 | [8 empty] | 1 | [22 empty] | 99 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Variable | Variable | N/A | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/PeripheralBatteryCabinets.aspx |  | Other,USB Port,Ethernet | Modbus TCP,Modbus RTU |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/SUMMITSeries.aspx | None | 2017-10-01 | 2017-11-01 | United States, Canada | ES_1138510_UPSU33E-A754DU-4_10302017134304_5857965
2310723 | Mitsubishi Electric Power Products, Inc. | Mitsubishi | 9900CX Series | 9900CX Series |  | Ac-output UPS | Static | UP9933C-A105DU-4 | 1000000 | 1050000 | UP9933C-B215DU-4 | 1995000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 384-552 | 54-66 | 494-466 | 60-60 | No |  | 2000 | 3003 | 900 | 0 | 0 | 0 | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 245600 |  | 96.4 |  | 97 |  | 96.9 |  | 96.7 |  | 96.8 | [8 empty] | 0.99 |  | 11035.09 |  | 95.9 |  | 96.7 |  | 96.6 |  | 96.6 |  | 96.5 | [8 empty] | 1 | 1 | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Variable | Variable | 36 months or 42 months | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/PeripheralBatteryCabinets.aspx |  | USB Port,Ethernet | Modbus TCP |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/products/Pages/9900C.aspx | None | 2017-10-01 | 2014-10-03 | United States, Canada | ES_1138510_9900CX Series_02122018111737_8106653
2174042 | Mitsubishi Electric Power Products, Inc. | Mitsubishi Electric | 9900A Series | 9900A Series |  | Ac-output UPS | Static | UP9933A-A234DU-4 | 202500 | 225000 | UP9933A-A234DU-4 |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2047 | 900 | 832 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 0 |  | 94.7 |  | 95.3 |  | 95.5 |  | 95.3 |  | 95.2 | [8 empty] | 0.99 | [22 empty] | 95.2 | NA | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 to 7 | 23 to 27 | 3 | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/9900A.aspx |  | Serial Port | None |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/9900A.aspx | None | 2013-02-01 | 2013-02-28 | United States | ES_1119276_9900A Series_02282013001930_7916223
2174552 | Mitsubishi Electric Power Products, Inc. | Mitsubishi Electric | 1100B Series | 1100B Series |  | Ac-output UPS | Static | UP1133B-A503SU-2 | 45000 | 50000 | UP1133B-A803SU-2 | 72000 |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 120-208 | 60-60 | 120-208 | 60-60 | Yes | 28 | 1714 | 800 | 686 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 0 |  | 0 |  | 94 |  | 94 |  | 94 |  | 94 | [8 empty] | 0.9 |  | 0 |  | 0 |  | 94 |  | 93.9 |  | 93 |  | 93.7 | [8 empty] | 0.9 | 0.9 | 94 | PMAU-02 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 18-5 | 36-10 | 2 | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/1100.aspx |  | Serial Port | None |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/1100.aspx | None | 2013-02-01 | 2013-03-05 | United States | ES_1119276_1100B Series_02282013161442_7411157
2174553 | Mitsubishi Electric Power Products, Inc. | Mitsubishi Electric | 9900B Series | 9900B Series |  | Ac-output UPS | Static | UP9933B-A754DU-4 | 675000 | 750000 | N/A |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2049 | 2302 | 832 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 0 |  | 95.7 |  | 96.7 |  | 96.7 |  | 96.4 |  | 96.4 | [8 empty] | 0.9 | [22 empty] | 96.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 to 15 | 10 to 30 | 3 | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/9900B.aspx |  | Serial Port | None |  | No |  | http://www.meppi.com/Products/UninterruptiblePowerSupplies/Products//Pages/9900B.aspx | None | 2013-02-01 | 2013-03-05 | United States | ES_1119276_9900B Series_02282013174552_3464167
2182255 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | E1500RTXL2U | E1500RTXL2U | E1500RT2U,E1500RT2U, | Ac-output UPS | Static | E1500RTXL2U | 2560 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-125 | 60-60 | 120-125 | 60-60 | Yes |  | 89 | 483 | 440 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 32.21 |  | 94 |  | 96.4 |  | 96.9 |  | 96.9 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | http://www.csb-battery.com/chine/01_product/02_detail.php?fid=7&pid=28 |  | None | None |  | Yes |  | http://www.delta.com.tw/ | http://www.csb-battery.com/chine/01_product/02_detail.php?fid=7&pid=28 | 2013-07-01 | 2016-03-16 | United States, Canada | ES_1105798_DELTA ELECTRONICS INC (175190) ¦ E1500RTXL2U_05302013020827_9707405
2182259 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | E1500RTXLT2U | E1500RTXLT2U |  | Ac-output UPS | Static | E1500RTXLT2U | 1200 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 89 | 282 | 442 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 240 | 60 | 240 | 60 | 32.26 |  | 94.9 |  | 96.6 |  | 96.9 |  | 96.7 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | http://www.minutemanups.com/products/enterprisepluslcd.php#page=page-1 | N/A | 2013-07-01 | 2014-10-22 | United States, Canada | ES_1105798_DELTA ELECTRONICS INC (175190) ¦ E1500RTXLT2U_06042013013131_9491793
2182260 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | E3000RTXLT2U | E3000RTXLT2U |  | Ac-output UPS | Static | E3000RTXLT2U | 2560 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 89 | 482 | 628 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 240 | 60 | 240 | 60 | 32.26 |  | 94.9 |  | 96.6 |  | 96.9 |  | 96.7 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | http://www.minutemanups.com/products/enterprisepluslcd.php#page=page-1 | N/A | 2013-07-01 | 2014-10-22 | United States, Canada | ES_1105798_DELTA ELECTRONICS INC (175190) ¦ E3000RTXLT2U_06042013013114_9474462
2221257 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED5200RTXL | ED5200RTXL(ED5000RT-CU;BP192RTXL) |  | Ac-output UPS | Static | ED5200RTXL(ED5000RT-CU;BR192RTXL) | 4500 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 88 | 440 | 660 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 144.24 |  | 93.4 |  | 96.2 |  | 97.2 |  | 97.6 |  | 97 | [8 empty] | 1 | [22 empty] | 97 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | Yes | 5 | 14 | 3 | N/A |  | Serial Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/products/endeavor_5-10kva_ups_systems.php | N/A | 2014-08-15 | 2016-03-29 | United States, Canada | ES_1123952_ED5200RTXL(ED5000RT-CU;BR192RTXL)_10062014063513_7313554
2223294 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | E2000RTXL2U | E2000RTXL2U | E2000RT2U,E2000RT2U, | Ac-output UPS | Static | E2000RTXL2U | 1760 | 2000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-125 | 50-60 | 120-125 | 50-60 | Yes |  | 89 | 482 | 616 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 25.87 |  | 93.5 |  | 96.7 |  | 97.2 |  | 97.4 |  | 97.1 | [8 empty] | 1 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | http://www.minutemanups.com/products/enterprisepluslcd.php#page=page-1 | N/A | 2013-07-01 | 2014-10-22 | United States, Canada | ES_1123952_E2000RTXL2U_10232014055147_3507324
2223295 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | E3000RTXL2U | E3000RTXL2U | E3000RT2U,E3000RT2U, | Ac-output UPS | Static | E3000RTXL2U | 2560 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-125 | 50-60 | 120-125 | 50-60 | Yes |  | 89 | 482 | 616 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 125 | 60 | 125 | 60 | 32.26 |  | 94.9 |  | 96.6 |  | 96.9 |  | 96.7 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 3 | N/A |  | None | None |  | Yes |  | http://www.minutemanups.com/products/enterprisepluslcd.php#page=page-1 | N/A | 2013-07-01 | 2014-10-22 | United States, Canada | ES_1123952_E3000RTXL2U_10232014055002_3402317
2231676 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED6200RTXL | ED6200RTXL(ED6000RT-CU;BP192RTXL) |  | Ac-output UPS | Static | ED6000RTXL(ED6000RT-CU;BR192RTXL) | 5400 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 177 | 440 | 660 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 132.14 |  | 94.2 |  | 96.7 |  | 95.7 |  | 93.1 |  | 90.1 | [8 empty] | 1 | [22 empty] | 90.1 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | Yes | 3 | 11 | 3 | N/A |  | Serial Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/products/endeavor_5-10kva_ups_systems.php | N/A | 2014-08-15 | 2016-03-29 | United States, Canada | ES_1123952_ED6200RTXL(ED6000RT-CU;BR192RTXL)_01142015075338_2018394
2231677 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED8200RTXL | ED8200RTXL(ED8000RT-CU;BP240RTXL) |  | Ac-output UPS | Static | ED8000RT-CU | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 261 | 440 | 625 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 179.69 |  | 94.9 |  | 95.3 |  | 96.8 |  | 96.6 |  | 96.2 | [8 empty] | 1 | [22 empty] | 96.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | Yes | 6 minutes | 16 minutes | 3 | N/A |  | Serial Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/products/endeavor_5-10kva_ups_systems.php | N/A | 2014-08-15 | 2012-09-26 | United States, Canada | ES_1123952_ED8200RTXL(ED8000RT-CU;BP240RTXL)_01142015075424_2064839
2231678 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED10200RTXL | ED10200RTXL(ED10000RT-CU;BP240RTXL) |  | Ac-output UPS | Static | ED10000RT-CU | 9000 | 10000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 261 | 440 | 625 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 168.53 |  | 95.3 |  | 95.9 |  | 95.1 |  | 95.9 |  | 95.5 | [8 empty] | 1 | [22 empty] | 95.5 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | Yes | 5 minutes | 12 minutes | 3 | N/A |  | Serial Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/products/endeavor_5-10kva_ups_systems.php | N/A | 2014-08-15 | 2012-09-26 | United States, Canada | ES_1123952_ED10200RTXL(ED10000RT-CU;BP240RTXL)_01142015075646_2206284
2288213 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | EC1500RT2U | EC1500RT2U |  | Ac-output UPS | Static | EC1500RT2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 110-120 | 50-60 | 110-120 | 50-60 | Yes |  | 89 | 440 | 475 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 30.5 |  | 83.6 |  | 88.3 |  | 89.4 |  | 89.5 |  | 89.1 | [8 empty] | 1 | [22 empty] | 89.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 15 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/ products/#page=page-1 | N/A | 2017-01-02 | 2017-01-03 | United States, Canada | ES_1123952_EC1500RT2U_01112017080353_1833596
2288214 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | EC1000RT2U | EC1000RT2U |  | Ac-output UPS | Static | EC1000RT2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 110-120 | 50-60 | 110-120 | 50-60 | Yes |  | 89 | 440 | 405 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.58 |  | 81.8 |  | 87.7 |  | 88.9 |  | 89.2 |  | 88.6 | [8 empty] | 1 | [22 empty] | 88.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/ products/#page=page-1 | N/A | 2017-01-02 | 2017-01-03 | United States, Canada | ES_1123952_EC1000RT2U_01112017083523_3723599
2288215 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | EC2000RT2U | EC2000RT2U |  | Ac-output UPS | Static | EC2000RT2U | 1800 | 2000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 110-120 | 50-60 | 110-120 | 50-60 | Yes |  | 89 | 440 | 475 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 29.7 |  | 86.4 |  | 89.8 |  | 90.4 |  | 90.1 |  | 90.1 | [8 empty] | 1 | [22 empty] | 90.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/ products/#page=page-1 | N/A | 2017-01-02 | 2017-01-03 | United States, Canada | ES_1123952_EC2000RT2U_01112017084537_4337206
2288223 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | EC3000RT2U | EC3000RT2U |  | Ac-output UPS | Static | EC3000RT2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer | 110-120 | 50-60 | 110-120 | 50-60 | Yes |  | 89 | 440 | 600 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 45.84 |  | 89.4 |  | 91.5 |  | 91.6 |  | 91.1 |  | 91.4 | [8 empty] | 1 | [22 empty] | 91.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 10 | 3 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | http://www.minutemanups.com/ products/#page=page-1 | N/A | 2017-01-02 | 2017-01-03 | United States, Canada | ES_1123952_EC3000RT2U_01112017085610_4970140
2290490 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED1000RTXL2U | ED1000RTXL2U |  | Ac-output UPS | Static | ED1000RTXL2U | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes |  | 89 | 482 | 339 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 28.3 |  | 84.8 |  | 89.4 |  | 90.2 |  | 89.8 |  | 89.8 | [8 empty] | 1 | [22 empty] | 89.8 | ED1000RTXL2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2017-05-31 | 2017-02-08 | United States | ES_1123952_ED1000RTXL2U_02132017054133_4493348
2290491 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED1500RTXL2U | ED1500RTXL2U |  | Ac-output UPS | Static | ED1500RTXL2U | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes |  | 89 | 482 | 432 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 28.5 |  | 88.9 |  | 91.6 |  | 92 |  | 91.7 |  | 91.8 | [8 empty] | 1 | [22 empty] | 91.8 | ED1500RTXL2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2017-05-31 | 2017-02-08 | United States | ES_1123952_ED1500RTXL2U_02132017054521_4721502
2290492 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED2000RTXL2U | ED2000RTXL2U |  | Ac-output UPS | Static | ED2000RTXL2U | 1800 | 2000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes |  | 89 | 482 | 432 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.24 |  | 89.9 |  | 92 |  | 92 |  | 91.4 |  | 91.8 | [8 empty] | 1 | [22 empty] | 91.8 | ED2000RTXL2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2017-05-31 | 2017-02-08 | United States | ES_1123952_ED2000RTXL2U_02132017060154_5714623
2290493 | Para Systems, Inc./Minuteman Power Technologies | Minuteman | ED3000RTXL2U | ED3000RTXL2U |  | Ac-output UPS | Static | ED3000RTXL2U | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial,Consumer,Data Center | 120-120 | 50-60 | 120-120 | 50-60 | Yes |  | 89 | 482 | 621 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 36.4 |  | 91.2 |  | 92.8 |  | 92.7 |  | 92 |  | 92.5 | [8 empty] | 1 | [22 empty] | 92.5 | ED3000RTXL2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | N/A | N/A | 2 | N/A |  | Serial Port,USB Port,Ethernet | Other,SNMP (v1, 2 or 3) |  | Yes |  | N/A | N/A | 2017-05-31 | 2017-02-08 | United States | ES_1123952_ED3000RTXL2U_02132017060802_6082643
2241854 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR1000LCD | ETR1000LCD |  | Ac-output UPS | Static | ETR1000LCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 410 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.338 |  | 98.1 |  | 98.5 |  | 98.4 |  | 98.1 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | N/A | Integral | No | N/A | N/A | N/A | N/A |  | USB Port | None |  | Yes |  | http://www.minutemanups.com/products/entrust.php#page=page-1 | N/A | 2015-05-04 | 2015-06-18 | United States, Canada | ES_1123952_ETR1000LCD_06172015172504_4000360
2241855 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR1500LCD | ETR1500LCD |  | Ac-output UPS | Static | ETR1500LCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 410 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.111 |  | 97.9 |  | 97.9 |  | 97.4 |  | 97 |  | 97.4 | [8 empty] | 1 | [22 empty] | 97.4 | N/A | Battery | N/A | Integral | No | N/A | N/A | N/A | N/A |  | USB Port | None |  | Yes |  | http://www.minutemanups.com/products/entrust.php#page=page-1 | N/A | 2015-05-04 | 2015-06-18 | United States, Canada | ES_1123952_ETR1500LCD_06172015192038_7389032
2243536 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR550LCD | ETR550LCD |  | Ac-output UPS | Static | ETR550LCD | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 288 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.27 |  | 94.6 |  | 96.4 |  | 97 |  | 97 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | N/A | Integral | No | N/A | N/A | N/A | N/A |  | USB Port | None |  | Yes |  | http://www.minutemanups.com/products/entrust.php#page=page-1 | N/A | 2015-05-04 | 2015-07-20 | United States, Canada | ES_1123952_ETR550LCD_07172015121822_8241845
2243789 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR700LCD | ETR700LCD |  | Ac-output UPS | Static | ETR700LCD | 420 | 700 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 288 |  |  |  | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.88 |  | 96.7 |  | 97.8 |  | 97.9 |  | 97.8 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | N/A | Integral | No | N/A | N/A | N/A | N/A |  | USB Port | None |  | Yes |  | http://www.minutemanups.com/products/entrust.php#page=page-1 | N/A | 2015-05-04 | 2015-07-20 | United States, Canada | ES_1123952_ETR700LCD_07172015121954_707513
2269776 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR550LCD | ETR550LCD |  | Ac-output UPS | Static | ETR550LCD | 330 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 288 | 6 | 3 | 3 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.36 |  | 94.6 |  | 96.5 |  | 97.2 |  | 97.2 |  | 96.9 | [8 empty] | 0.99 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-09-28 | 2017-05-01 | United States | ES_1123952_ETR550LCD_06082016050408_8332720
2269777 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR700LCD | ETR700LCD |  | Ac-output UPS | Static | ETR700LCD | 420 | 700 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 288 | 12 | 12 | 6 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.33 |  | 95.5 |  | 97 |  | 97.1 |  | 96.8 |  | 96.9 | [8 empty] | 0.99 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-09-28 | 2017-05-01 | United States | ES_1123952_ETR700LCD_06152016065104_8693813
2269778 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR1000LCD | ETR1000LCD |  | Ac-output UPS | Static | ETR1000LCD | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 410 | 16 | 16 | 8 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.5 |  | 97.1 |  | 97.7 |  | 97.4 |  | 97 |  | 97.3 | [8 empty] | 0.99 | [22 empty] | 97.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-09-28 | 2016-06-03 | United States | ES_1123952_ETR1000LCD_06152016070555_1659128
2269779 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | ETR1500LCD | ETR1500LCD |  | Ac-output UPS | Static | ETR1500LCD | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 280 | 87 | 410 | 16 | 16 | 8 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.79 |  | 97.6 |  | 97.6 |  | 97.2 |  | 96.7 |  | 97.1 | [8 empty] | 0.99 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-09-28 | 2016-06-03 | United States | ES_1123952_ETR1500LCD_06152016072331_6722484
2283721 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | EN750LCD | EN750LCD |  | Ac-output UPS | Static | EN750LCD | 450 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 92 | 183 | 320 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.53 |  | 96.1 |  | 97.3 |  | 97.3 |  | 96.9 |  | 96.9 | [8 empty] | 0.99 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-11-11 | 2016-11-10 | United States | ES_1123952_EN750LCD _10252016034212_4263239
2284566 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | EN550 | EN550 |  | Ac-output UPS | Static | EN550 | 300 | 550 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 94 | 130 | 316 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.26 |  | 95.4 |  | 97.1 |  | 97.2 |  | 97.1 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 3 | 11 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2016-11-22 | 2016-11-17 | United States | ES_1123952_EN550_11172016032653_4208769
2288046 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | EN900LCD | EN900LCD |  | Ac-output UPS | Static | EN900LCD | 500 | 900 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 92 | 183 | 320 | 10 | 10 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.61 |  | 96.7 |  | 97.5 |  | 97.1 |  | 96.7 |  | 96.9 | [8 empty] | 0.99 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 10 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2017-01-10 | 2017-01-05 | United States | ES_1123952_EN900LCD_01052017024420_8018724
2312529 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | PRO1000RT2U | PRO1000RT2U |  | Ac-output UPS | Static | PRO1000RT2U | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 86 | 480 | 410 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.53 |  | 96.5 |  | 97.6 |  | 97.8 |  | 97.6 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4 | 14 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2018-06-01 | 2018-03-09 | United States, Canada | ES_1123952_PRO1000RT2U_03072018054851_3882532
2312530 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | PRO750RT2U | PRO750RT2U |  | Ac-output UPS | Static | PRO750RT2U | 525 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 86 | 480 | 410 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.62 |  | 95.6 |  | 97.3 |  | 97.8 |  | 97.9 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 14 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2018-06-01 | 2018-03-09 | United States, Canada | ES_1123952_PRO750RT2U_03072018053130_2620116
2318925 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | EN350 | EN350 |  | Ac-output UPS | Static | EN350 | 200 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 94 | 130 | 316 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.35 |  | 93.7 |  | 96.7 |  | 97.6 |  | 98 |  | 96.7 | [8 empty] | 0.99 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3 | 12 | 1 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2018-05-01 | 2018-04-26 | United States, Canada | ES_1123952_EN350_04262018051247_6720593
2319657 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | PRO2000RT2U | PRO2000RT2U |  | Ac-output UPS | Static | PRO2000RT2U | 1400 | 2000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 86 | 480 | 510 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.88 |  | 98 |  | 97.7 |  | 98.2 |  | 97.8 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4 | 14 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2018-06-01 | 2018-05-11 | United States, Canada | ES_1123952_PRO2000RT2U_05082018022320_8575910
2319658 | Para Systems, Inc./Minuteman Power Technologies | MINUTEMAN Power Technologies | PRO1500RT2U | PRO1500RT2U |  | Ac-output UPS | Static | PRO1500RT2U | 1050 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 86 | 480 | 510 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.79 |  | 97.2 |  | 98 |  | 98.1 |  | 97.9 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4 | 14 | 3 | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 |  | USB Port | None |  | No |  | http://www.minutemanups.com/products/entrust_lcd_avr_tower_ups.php#page=page-1 | N/A | 2018-06-01 | 2018-05-11 | United States, Canada | ES_1123952_PRO1500RT2U_05082018020752_9742659
2233776 | Piller Group GmbH | Piller UNIBLOCK | UBT+1800 | UBT+1800 | ,UBT+1500,rated 1500kW 400V, 50 Hz.; ,UBT+1800,rated 1800kW 480V, 60Hz.; ,UBTD+1500,rated 1500kW 400V, 50 Hz., D represents diesel model option; ,UBTD+1800,rated 1800kW 480V, 60Hz., D represents diesel model option | Ac-output UPS | Rotary | 1 | 1500000 | 1670000 | 1 | 1800000 |  | Line Interactive | ac Line Interactive (VI) | Commercial,Data Center | 400-480 | 50-60 | 400-480 | 50-60 | No | 0 | 2700 | 4600 | 1320 | 1 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 472 | 60 | 482 | 60 | 44000 |  | 91.1 |  | 94.9 |  | 96.1 |  | 96.2 |  | 94.3 | [8 empty] | 0.98 | [22 empty] | 94.3 | 1 | Flywheel | Flywheel | Separate Enclosure | Yes | .18 for flywheel or dependent on battery supplied | .37 for flywheel or dependent on battery supplied | negotiated in contract | http://www.piller.com/205/energy-storage |  | Ethernet | Modbus TCP | Modbus | No |  | http://www.piller.com/ | IEC 62040-3 Annex J | 2014-04-01 | 2014-08-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095905_UBT+1800_11262014153045_3576471
2256252 | Piller Group GmbH | Piller UNIBLOCK | UBT+1200 | UBT+1200 | ,UBT+1000,rated 1000kW 400V, 50 Hz.; ,UBT+1200,rated 1200kW 480V 60Hz.; ,UBTD+1000,rated 1000kW 400V, 50 Hz., D represents diesel model option; ,UBTD+1200,rated 1200kW 480V 60Hz., D represents diesel model option | Ac-output UPS | Rotary | 1 | 1000000 | 1100000 | 1 | 1200000 |  | Line Interactive | ac Line Interactive (VI) | Commercial,Data Center | 400-480 | 50-60 | 400-480 | 50-60 | No | 0 | 2700 | 4600 | 1320 | 1 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 402 | 50 | 401 | 50 | 25700 |  | 91 |  | 94.8 |  | 96.1 |  | 96.5 |  | 94.2 | [8 empty] | 0.98 | [22 empty] | 94.2 | 1 | Flywheel | Flywheel | Separate Enclosure | Yes | .27 for flywheel or dependent on battery supplied | .53 for flywheel or dependent on battery supplied | negotiated in contract | http://www.piller.com/205/energy-storage |  | Ethernet | Modbus TCP | Modbus | No |  | http://www.piller.com/ | IEC 62040-3 Annex J | 2014-04-01 | 2014-08-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1095905_UBT+1200_12172015114721_2025415
2167123 | Schneider Electric | APC | Symmetra PX250 | SY100K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250D_01092013021805_7885848
2167124 | Schneider Electric | APC | Symmetra PX250 | SY100K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DL-PD_01092013021826_7906543
2167125 | Schneider Electric | APC | Symmetra PX250 | SY100K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DR-PD_01092013021846_7926999
2167126 | Schneider Electric | APC | Symmetra PX250 | SY125K250-X676 |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250-X676_01092013023749_9069974
2167127 | Schneider Electric | APC | Symmetra PX250 | SY125K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D_01092013023802_9082677
2167128 | Schneider Electric | APC | Symmetra PX250 | SY125K250D-NB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D-NB_01092013023816_9096799
2167129 | Schneider Electric | APC | Symmetra PX250 | SY125K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PD_01092013023831_9111576
2167130 | Schneider Electric | APC | Symmetra PX250 | SY125K250DL-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PDNB_01092013023847_9127578
2167131 | Schneider Electric | APC | Symmetra PX250 | SY125K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PD_01092013023901_9141577
2167132 | Schneider Electric | APC | Symmetra PX250 | SY125K250DR-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PDNB_01092013023914_9154228
2167133 | Schneider Electric | APC | Symmetra PX500 | SY125K500-X676 |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500-X676_01092013025203_9923782
2167134 | Schneider Electric | APC | Symmetra PX500 | SY125K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D_01092013025217_9937266
2167135 | Schneider Electric | APC | Symmetra PX500 | SY125K500D-NB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D-NB_01092013025230_9950866
2167136 | Schneider Electric | APC | Symmetra PX250 | SY150K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250D_01092013024422_9462932
2167137 | Schneider Electric | APC | Symmetra PX250 | SY150K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DL-PD_01092013024435_9475842
2167138 | Schneider Electric | APC | Symmetra PX250 | SY150K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DR-PD_01092013024449_9489244
2167139 | Schneider Electric | APC | Symmetra PX250 | SY200K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250D_01092013024841_9721789
2167140 | Schneider Electric | APC | Symmetra PX250 | SY200K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DL-PD_01092013024855_9735394
2167141 | Schneider Electric | APC | Symmetra PX250 | SY200K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DR-PD_01092013024908_9748978
2167156 | Schneider Electric | APC | Symmetra PX500 | SY125K500DL-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PDNB_01092013103438_7678073
2167157 | Schneider Electric | APC | Symmetra PX500 | SY125K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PD_01092013103450_7690632
2167158 | Schneider Electric | APC | Symmetra PX500 | SY125K500DR-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PDNB_01092013103503_7703930
2167159 | Schneider Electric | APC | Symmetra PX500 | SY250K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500D_01092013103923_7963573
2167160 | Schneider Electric | APC | Symmetra PX500 | SY250K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DL-PD_01092013103936_7976747
2167161 | Schneider Electric | APC | Symmetra PX500 | SY250K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DR-PD_01092013103949_7989182
2167162 | Schneider Electric | APC | Symmetra PX500 | SY300K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500D_01092013104002_8002070
2167163 | Schneider Electric | APC | Symmetra PX500 | SY300K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DL-PD_01092013104014_8014607
2167164 | Schneider Electric | APC | Symmetra PX500 | SY300K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DR-PD_01092013104027_8027104
2167165 | Schneider Electric | APC | Symmetra PX500 | SY400K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500D_01092013104345_8225810
2167166 | Schneider Electric | APC | Symmetra PX500 | SY400K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DL-PD_01092013104357_8237668
2167167 | Schneider Electric | APC | Symmetra PX500 | SY400K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DR-PD_01092013104410_8250034
2167168 | Schneider Electric | APC | Symmetra PX500 | SY500K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500D_01092013104702_8422137
2167169 | Schneider Electric | APC | Symmetra PX500 | SY500K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DL-PD_01092013104713_8433724
2167170 | Schneider Electric | APC | Symmetra PX500 | SY500K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DR-PD_01092013104726_8446841
2167171 | Schneider Electric | APC | Symmetra PX500 | SY125K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PD_01092013103424_7664475
2185262 | Schneider Electric | APC | APC Smart-UPS 1500VA LCD RM 2U 120V | SMT1500RMUS |  | Ac-output UPS | Static | SMT1500RM2U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.88 |  | 96.3 |  | 97.5 |  | 97.6 |  | 97.4 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.2 | 25.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC136 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-03-02 | 2013-07-09 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500RMUS_07102013174224_8144991
2260126 | Schneider Electric | APC | Symmetra PX 100kW Scalable to 100kW 208V with Startup | SY100K100F | Symmetra PX 100kW Scalable to 100kW 208V with Startup No Battery,SY100K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY100K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY100K100F_01282016215045_7845338
2260127 | Schneider Electric | APC | Symmetra PX 10kW Scalable to 100kW 208V with Startup | SY10K100F | Symmetra PX 10kW Scalable to 100kW 208V with Startup No Battery,SY10K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY10K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY10K100F_01282016212453_6293262
2260128 | Schneider Electric | APC | Symmetra PX 20kW Scalable to 100kW 208V with Startup | SY20K100F | Symmetra PX 20kW Scalable to 100kW 208V with Startup No Battery,SY20K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY20K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY20K100F_01282016212929_6569719
2260129 | Schneider Electric | APC | Symmetra PX 30kW Scalable to 100kW 208V with Startup | SY30K100F | Symmetra PX 30kW Scalable to 100kW 208V with Startup No Battery,SY30K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY30K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY30K100F_01282016213058_6658414
2260130 | Schneider Electric | APC | Symmetra PX 40kW Scalable to 100kW 208V with Startup | SY40K100F | Symmetra PX 40kW Scalable to 100kW 208V with Startup No Battery,SY40K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY40K100F_01282016213338_6818900
2260131 | Schneider Electric | APC | Symmetra PX 50kW Scalable to 100kW 208V with Startup | SY50K100F | Symmetra PX 50kW Scalable to 100kW 208V with Startup No Battery,SY50K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY50K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY50K100F_01282016213535_6935431
2260132 | Schneider Electric | APC | Symmetra PX 60kW Scalable to 100kW 208V with Startup | SY60K100F | Symmetra PX 60kW Scalable to 100kW 208V with Startup No Battery,SY60K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY60K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY60K100F_01282016213702_7022721
2260133 | Schneider Electric | APC | Symmetra PX 70kW Scalable to 100kW 208V with Startup | SY70K100F | Symmetra PX 70kW Scalable to 100kW 208V with Startup No Battery,SY70K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY70K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY70K100F_01282016213816_7096964
2260134 | Schneider Electric | APC | Symmetra PX 80kW Scalable to 100kW 208V with Startup | SY80K100F | Symmetra PX 80kW Scalable to 100kW 208V with Startup No Battery,SY80K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY80K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY80K100F_01282016214654_7614982
2260135 | Schneider Electric | APC | Symmetra PX 90kW Scalable to 100kW 208V with Startup | SY90K100F | Symmetra PX 90kW Scalable to 100kW 208V with Startup No Battery,SY90K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY90K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY90K100F_01282016214931_7771863
2181721 | Schneider Electric | APC by Schneider Electric | APC Back-UPS Pro 500 Lithium Ion UPS | BG500 | APC Back-UPS Pro 500 Lithium Ion UPS,BG500,; APC Back-UPS Pro 500 Lithium Ion UPS,BG500Q,; APC Back-UPS Pro 500 Lithium Ion UPS,BG500W, | Ac-output UPS | Static | BG500 | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 54 | 290 | 191 | 4 | 4 | 0 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.54 |  | 95.4 |  | 97.6 |  | 98.2 |  | 98.6 |  | 97.6 | [8 empty] | 1 | [22 empty] | 97.6 | N/A | Battery | Lithium-ion Battery | Integral | N/A | 3.57 | 8.2 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC146-Li | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | Ethernet | HTTP |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BG500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2013-09-09 | 2013-10-02 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BG500_05292013003624_7784974
2185257 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 1U 120V | SMT1500RM1U | APC Smart-UPS 1500VA LCD RM 1U 120V,SMT1500RM1U,; APC Smart-UPS 1500VA LCD RM 1U 120V,SMT1500RM1UQ,; APC Smart-UPS 1500VA LCD RM 1U 120V,SMT1500RM1UQW, | Ac-output UPS | Static | SMT1500RM1U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 1 | 44 | 432 | 665 | 4 | 4 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 10.96 |  | 95.6 |  | 97.5 |  | 98.1 |  | 98.3 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5 | 15.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC88 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500RM1U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2013-08-30 | 2013-07-09 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500RM1U_07102013174139_8099624
2185260 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V | SMT1500RM2U | ,SMT1500R2X122,; APC Smart-UPS 1500VA LCD RM 2U 120V,SMT1500RM2U,; APC Smart-UPS 1500VA LCD RM 2U 120V,SMT1500RM2UQ,; APC Smart-UPS 1500VA LCD RM 2U 120V,SMT1500RM2UQW, | Ac-output UPS | Static | SMT1500RM2U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.88 |  | 96.3 |  | 97.5 |  | 97.6 |  | 97.4 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.2 | 25.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC134 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-03-02 | 2013-07-09 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500RM2U_07102013174206_8126529
2185263 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V | SMT1500RMUS |  | Ac-output UPS | Static | SMT1500RM2U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.88 |  | 96.3 |  | 97.5 |  | 97.6 |  | 97.4 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.2 | 25.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC137 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-03-02 | 2013-07-09 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500RMUS_07102013174234_8154128
2185308 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 750VA LCD 120V | SMT750US | APC Smart-UPS 750VA LCD 120V,SMT750US,; APC Smart-UPS 750VA LCD 120V,SMT750USQ,; APC Smart-UPS 750VA LCD 120V,SMT750USW, | Ac-output UPS | Static | SMT750 | 500 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 161 | 138 | 363 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.56 |  | 94.1 |  | 96.7 |  | 97.5 |  | 97.9 |  | 97.4 | [8 empty] | 0.99 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.6 | 15.9 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC48 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT750 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-30 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT750US_07102013211546_0946075
2188698 | Schneider Electric | APC by Schneider Electric | APC Back-UPS 650 | BE650G1 | APC Back-UPS 650,BE650G1,; APC Back-UPS 650,BE650G1Q,; APC Back-UPS 650,BE650G1W, | Ac-output UPS | Static | BE650G1 | 390 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 88 | 180 | 302 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.39 |  | 97.5 |  | 98.6 |  | 99 |  | 99.1 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.3 | 12 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC17 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BE650G1 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-07-29 | 2013-08-19 | United States | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BE650G1_08232013042549_1949781
2188699 | Schneider Electric | APC by Schneider Electric | APC Back-UPS 650, Canada | BE650G1-CN | APC Back-UPS 650, Canada,BE650G1-CN,; APC Back-UPS 650, Canada,BE650G1-CNQ,; APC Back-UPS 650, Canada,BE650G1-CNW, | Ac-output UPS | Static | BE650G1 | 390 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 88 | 180 | 302 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.39 |  | 97.5 |  | 98.6 |  | 99 |  | 99.1 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.3 | 12 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC17 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BE650G1-CN | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-07-29 | 2013-08-19 | Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BE650G1-CN_08232013043330_2410906
2188702 | Schneider Electric | APC by Schneider Electric | APC Back-UPS 350 | BK350 | APC Back-UPS 350,BK350,; APC Back-UPS 350,BK350Q,; APC Back-UPS 350,BK350W, | Ac-output UPS | Static | BK350 | 210 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 165 | 91 | 284 | 6 | 3 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.09 |  | 96.1 |  | 97.9 |  | 98.5 |  | 98.8 |  | 98 | [8 empty] | 1 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 5.6 | 20.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC2 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BK350 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2012-10-25 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BK350_08232013043044_2244407
2188703 | Schneider Electric | APC by Schneider Electric | APC APC Back-UPS 350VA X545 120V | BK350X545 | APC APC Back-UPS 350VA X545 120V,BK350X545,; APC APC Back-UPS 350VA X545 120V,BK350X545Q,; APC APC Back-UPS 350VA X545 120V,BK350X545W, | Ac-output UPS | Static | BK350 | 210 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 165 | 91 | 284 | 6 | 3 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.09 |  | 96.1 |  | 97.9 |  | 98.5 |  | 98.8 |  | 98 | [8 empty] | 1 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.7 | 18.1 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC2J | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BK350X545 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2012-10-25 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BK350X545_08232013042637_1997587
2188705 | Schneider Electric | APC by Schneider Electric | APC Back-UPS 500 | BK500 | APC Back-UPS 500,BK500,; APC Back-UPS 500,BK500Q,; APC Back-UPS 500,BK500W, | Ac-output UPS | Static | BK500 | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 165 | 91 | 284 | 6 | 3 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.18 |  | 97.1 |  | 98.4 |  | 98.8 |  | 99 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.4 | 15.4 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC2 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BK500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2004-07-03 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BK500_08232013043126_2286178
2188707 | Schneider Electric | APC by Schneider Electric | APC Back-UPS 500 (black) | BK500BLK | APC Back-UPS 500 (black),BK500BLK,; APC Back-UPS 500 (black),BK500BLKQ,; APC Back-UPS 500 (black),BK500BLKW, | Ac-output UPS | Static | BK500 | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 165 | 91 | 284 | 6 | 3 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.18 |  | 97.1 |  | 98.4 |  | 98.8 |  | 99 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.4 | 15.4 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC2 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BK500BLK | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2004-07-03 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BK500BLK_08232013042651_2011393
2188710 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS NS 1080VA | BN1080G | APC Power Saving Back-UPS NS 1080VA,BN1080GQ,; APC Power Saving Back-UPS NS 1080VA,BN1080GW, | Ac-output UPS | Static | BN1080G | 650 | 1080 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 250 | 100 | 382 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.24 |  | 97.3 |  | 98.4 |  | 98.7 |  | 98.8 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.9 | 12.8 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC123 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BN1080G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2013-03-14 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BN1080G_08232013043552_2552425
2188712 | Schneider Electric | APC by Schneider Electric | APC Power-Saving Back-UPS Pro 1000 | BR1000G | APC Power-Saving Back-UPS Pro 1000,BR1000G,; APC Power-Saving Back-UPS Pro 1000,BR1000GQ,; APC Power-Saving Back-UPS Pro 1000,BR1000Q,; APC Power-Saving Back-UPS Pro 1000,BR1000W, | Ac-output UPS | Static | BR1000G | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 250 | 100 | 382 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.13 |  | 96.5 |  | 98 |  | 98.4 |  | 98.5 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.7 | 14.5 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC123 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BR1000G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-03-18 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BR1000G_08232013042730_2050466
2188713 | Schneider Electric | APC by Schneider Electric | APC Power-Saving Back-UPS Pro 1300 | BR1300G | APC Power-Saving Back-UPS Pro 1300,BR1300G,; APC Power-Saving Back-UPS Pro 1300,BR1300GQ,; APC Power-Saving Back-UPS Pro 1300,BR1300GW, | Ac-output UPS | Static | BR1300G | 780 | 1300 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.89 |  | 96.8 |  | 97.9 |  | 98.1 |  | 98.1 |  | 98 | [8 empty] | 1 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.7 | 14.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC124 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BR1300G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-05-27 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BR1300G_08232013042916_2156186
2188714 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS Pro 1500 | BR1500G | APC Power Saving Back-UPS Pro 1500,BR1500G,; APC Power Saving Back-UPS Pro 1500,BR1500GQ,; APC Power Saving Back-UPS Pro 1500,BR1500GW, | Ac-output UPS | Static | BR1500G | 865 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.69 |  | 97.2 |  | 98.1 |  | 98.3 |  | 98.2 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.8 | 12.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC124 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BR1500G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-05-27 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BR1500G_08232013042742_2062259
2188715 | Schneider Electric | APC by Schneider Electric | APC Power-Saving Back-UPS Pro 700 | BR700G | APC Power-Saving Back-UPS Pro 700,BR700G,; APC Power-Saving Back-UPS Pro 700,BR700GQ,; APC Power-Saving Back-UPS Pro 700,BR700GW, | Ac-output UPS | Static | BR700G | 420 | 700 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 190 | 91 | 310 | 6 | 3 | 3 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.01 |  | 96.2 |  | 97.9 |  | 98.4 |  | 98.6 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.1 | 13.2 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC17 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BR700G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-09-24 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BR700G_08232013043421_2461868
2188717 | Schneider Electric | APC by Schneider Electric | APC Power-saving Back-UPS XS 1000VA 120V Candada | BX1000G-CA | APC Power-saving Back-UPS XS 1000VA 120V Candada,BX1000G-CA,; APC Power-saving Back-UPS XS 1000VA 120V Candada,BX1000G-CAQ,; APC Power-saving Back-UPS XS 1000VA 120V Candada,BX1000G-CAW,; APC Power-saving Back-UPS XS 1000VA 120V Candada,BX1000GQ, | Ac-output UPS | Static | BX1000G | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 250 | 100 | 382 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.4 |  | 96.4 |  | 98 |  | 98.4 |  | 98.6 |  | 98 | [8 empty] | 1 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.5 | 16 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC123 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BX1000G-CA | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-02-03 | 2013-08-19 | Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BX1000G-CA_08232013043506_2506187
2188718 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS XS 1300 | BX1300G | APC Power Saving Back-UPS XS 1300,BX1300G,; APC Power Saving Back-UPS XS 1300,BX1300GQ,; APC Power Saving Back-UPS XS 1300,BX1300GW, | Ac-output UPS | Static | BX1300G-CA | 780 | 1300 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.65 |  | 97.4 |  | 98.4 |  | 98.5 |  | 98.5 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.3 | 9.8 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC123 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BX1300G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-08-14 | 2013-08-19 | United States | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BX1300G_08232013042808_2088558
2188719 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS XS 1300VA 120V Canada | BX1300G-CA | APC Power Saving Back-UPS XS 1300VA 120V Canada,BX1300G-CA,; APC Power Saving Back-UPS XS 1300VA 120V Canada,BX1300G-CAQ,; APC Power Saving Back-UPS XS 1300VA 120V Canada,BX1300G-CAW, | Ac-output UPS | Static | BX1300G-CA | 780 | 1300 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.65 |  | 97.4 |  | 98.4 |  | 98.5 |  | 98.5 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.3 | 9.8 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC123 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BX1300G-CA | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-08-14 | 2013-08-19 | Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BX1300G-CA_08232013042954_2194256
2188720 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS XS 1500 | BX1500G | APC Power Saving Back-UPS XS 1500,BX1500GQ,; APC Power Saving Back-UPS XS 1500,BX1500GW, | Ac-output UPS | Static | BX1500G | 865 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.69 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.5 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.8 | 12.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC124 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BX1500G | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-08-23 | 2013-08-19 | United States | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BX1500G_08232013042822_2102556
2188721 | Schneider Electric | APC by Schneider Electric | APC Power Saving Back-UPS XS 1500VA 120V Canada | BX1500G-CA | APC Power Saving Back-UPS XS 1500VA 120V Canada,BX1500G-CAQ,; APC Power Saving Back-UPS XS 1500VA 120V Canada,BX1500G-CAW, | Ac-output UPS | Static | BX1500G | 865 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 301 | 112 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.69 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.5 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.8 | 12.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC124 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=BX1500G-CA | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-08-23 | 2013-08-19 | Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ BX1500G-CA_08232013042423_1863576
2188722 | Schneider Electric | APC by Schneider Electric | APC AV J Type 1.5kVA Power Conditioner with | J25B | APC AV J Type 1.5kVA Power Conditioner with Battery Backup 120V,,; APC AV J Type 1.5kVA Power Conditioner with Battery Backup 120V,,; APC AV J Type 1.5kVA Power Conditioner with,J25B, | Ac-output UPS | Static | J25B | 865 | 1500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 431 | 406 | 8 | 6 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.56 |  | 97.3 |  | 98.2 |  | 98.4 |  | 98.3 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.7 | 12.3 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC131 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=J25B | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-01-11 | 2013-08-19 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ J25B_08232013045309_3589544
2189963 | Schneider Electric | APC by Schneider Electric | Symmetra PX40 | SY10K40F |  | Ac-output UPS | Static | SY10K40F | 10000 | 10000 | SY40K40F | 40000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 600 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 180.31 |  | 91.4 |  | 93.8 |  | 94.2 |  | 94 |  | 94 | [8 empty] | 1 |  | 525.5 |  | 92.9 |  | 94.5 |  | 94.6 |  | 94.4 |  | 94.2 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 13 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K40F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ SY10K40F_09092013184807_2487189
2189964 | Schneider Electric | APC by Schneider Electric | Symmetra PX40 | SY20K40F |  | Ac-output UPS | Static | SY10K40F | 10000 | 10000 | SY40K40F | 40000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 600 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 180.31 |  | 91.4 |  | 93.8 |  | 94.2 |  | 94 |  | 94 | [8 empty] | 1 |  | 525.5 |  | 92.9 |  | 94.5 |  | 94.6 |  | 94.4 |  | 94.2 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 13 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K40F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ SY20K40F_09092013184841_2521180
2189965 | Schneider Electric | APC by Schneider Electric | Symmetra PX40 | SY30K40F |  | Ac-output UPS | Static | SY10K40F | 10000 | 10000 | SY40K40F | 40000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 600 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 180.31 |  | 91.4 |  | 93.8 |  | 94.2 |  | 94 |  | 94 | [8 empty] | 1 |  | 525.5 |  | 92.9 |  | 94.5 |  | 94.6 |  | 94.4 |  | 94.2 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 13 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K40F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ SY30K40F_09092013184905_2545925
2189966 | Schneider Electric | APC by Schneider Electric | Symmetra PX40 | SY40K40F |  | Ac-output UPS | Static | SY10K40F | 10000 | 10000 | SY40K40F | 40000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 600 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 180.31 |  | 91.4 |  | 93.8 |  | 94.2 |  | 94 |  | 94 | [8 empty] | 1 |  | 525.5 |  | 92.9 |  | 94.5 |  | 94.6 |  | 94.4 |  | 94.2 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 13 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K40F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ SY40K40F_09092013184927_2567436
2189967 | Schneider Electric | APC by Schneider Electric | Symmetra PX20 | ISX10K20F |  | Ac-output UPS | Static | ISX10K20F | 10000 | 10000 | ISX20K20F | 20000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 610 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 181 |  | 91.6 |  | 93.8 |  | 94.2 |  | 94.1 |  | 94 | [8 empty] | 1 |  | 296 |  | 92.5 |  | 94.3 |  | 94.6 |  | 94.3 |  | 93.9 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 15 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=ISX20K20F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ ISX10K20F_09092013203807_9087675
2189968 | Schneider Electric | APC by Schneider Electric | Symmetra PX20 | ISX20K20F |  | Ac-output UPS | Static | ISX10K20F | 10000 | 10000 | ISX20K20F | 20000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2070 | 610 | 902 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 181 |  | 91.6 |  | 93.8 |  | 94.2 |  | 94.1 |  | 94 | [8 empty] | 1 |  | 296 |  | 92.5 |  | 94.3 |  | 94.6 |  | 94.3 |  | 93.9 | [8 empty] | 1 | 1 | 94 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 Minutes | 15 Minutes | One year | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBT4 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=ISX20K20F | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-01-01 | 2013-09-06 | United States, Canada | ES_1105798_APC DENMARK A/S (198152) ¦ ISX20K20F_09092013203855_9135208
2194866 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 750VA LCD 120V | SMT750 | APC Smart-UPS 750VA LCD 120V,SMT750,; APC Smart-UPS 750VA LCD 120V,SMT750Q,; APC Smart-UPS 750VA LCD 120V,SMT750W, | Ac-output UPS | Static | SMT750 | 500 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 161 | 138 | 363 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.6 |  | 94.1 |  | 96.7 |  | 97.5 |  | 97.9 |  | 97.4 | [8 empty] | 0.99 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.6 | 15.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC48 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT750 | N/A | 2009-10-30 | 2012-08-24 | United States, Canada | ES_1105798_American Power Conversion Corp (345126) ¦ SMT750_11182013163658_2618258
2194874 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V | SMX1500RM2U |  | Ac-output UPS | Static | SMX1500RM2U | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 9.48 |  | 96.6 |  | 97.9 |  | 98.1 |  | 98.1 |  | 98 | [8 empty] | 1 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC115 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-02 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX1500RM2U_11182013173504_6104323
2194876 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V | SMX1500RM2UNC | APC Smart-UPS X 1500VA Rack/Tower LCD 120V,SMX1500RM2UNC,; APC Smart-UPS X 1500VA Rack/Tower LCD 120V,SMX1500RM2UNCQ,; APC Smart-UPS X 1500VA Rack/Tower LCD 120V,SMX1500RM2UNCW, | Ac-output UPS | Static | SMX1500RM2UNC | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.36 |  | 96.1 |  | 97.6 |  | 97.9 |  | 98 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC115 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX1500RM2UNC | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-07 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX1500RM2UNC_11182013173656_6216879
2194878 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS RT 15kVA RM 208V | SURT15KRMXLT | APC Smart-UPS RT 15kVA RM 208V,SURT15KRMXLT,; APC Smart-UPS RT 15kVA RM 208V,SURT15KRMXLTQ,; APC Smart-UPS RT 15kVA RM 208V,SURT15KRMXLTW, | Ac-output UPS | Static | SURT15KRMXLT | 12000 | 15000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 208-208 | 50-60 | 208-208 | 50-60 | Yes | 12 | 533 | 432 | 773 | 6 | 6 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 175.78 |  | 92.3 |  | 94.4 |  | 94.8 |  | 94.8 |  | 94 | [8 empty] | 1 | [22 empty] | 94 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8.3 | 22.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC44 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | Simple Signaling, UPS-Lin | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SURT15KRMXLT | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-04-04 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SURT15KRMXLT_11182013174052_6452916
2194880 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS RT 20kVA RM 208V | SURT20KRMXLT | APC Smart-UPS RT 20kVA RM 208V,SURT20KRMXLT,; APC Smart-UPS RT 20kVA RM 208V,SURT20KRMXLTQ,; APC Smart-UPS RT 20kVA RM 208V,SURT20KRMXLTW, | Ac-output UPS | Static | SURT20KRMXLT | 16000 | 20000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Commercial | 208-208 | 50-60 | 208-208 | 50-60 | Yes | 12 | 533 | 432 | 773 | 6 | 6 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 179.52 |  | 93.4 |  | 94.8 |  | 94.8 |  | 94.6 |  | 94.5 | [8 empty] | 1 | [22 empty] | 94.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 4.9 | 15.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC44 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | Simple Signaling, UPS-Lin | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SURT20KRMXLT | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-04-04 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SURT20KRMXLT_11182013174348_6628495
2194882 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY100K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250D_11182013174623_6783177
2194884 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY100K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DL-PD_11182013174833_6913037
2194886 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY100K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DR-PD_11182013174950_6990675
2195042 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1000VA LCD 120V | SMC1000 | APC Smart-UPS C 1000VA LCD 120V,SMC1000,; APC Smart-UPS C 1000VA LCD 120V,SMC1000Q,; APC Smart-UPS C 1000VA LCD 120V,SMC1000W, | Ac-output UPS | Static | SMC1000 | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.26 |  | 94.6 |  | 97 |  | 97.8 |  | 98.1 |  | 97.7 | [8 empty] | 0.98 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6 | 16.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC142 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMC1000 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-29 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMC1000_11192013164726_9646514
2195044 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1000VA 2U LCD 120V | SMC1000-2U | APC Smart-UPS C 1000VA 2U LCD 120V,SMC1000-2U,; APC Smart-UPS C 1000VA 2U LCD 120V,SMC1000-2UQ,; APC Smart-UPS C 1000VA 2U LCD 120V,SMC1000-2UW, | Ac-output UPS | Static | SMC1000-2U | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 406 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.2 |  | 94.6 |  | 97 |  | 97.7 |  | 98 |  | 97.6 | [8 empty] | 0.98 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6 | 16.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC124 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMC1000-2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-12-01 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMC1000-2U_11192013164822_9702409
2195046 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1500VA LCD 120V | SMC1500 | APC Smart-UPS C 1500VA LCD 120V,SMC1500,; APC Smart-UPS C 1500VA LCD 120V,SMC1500Q,; APC Smart-UPS C 1500VA LCD 120V,SMC1500W, | Ac-output UPS | Static | SMC1500 | 900 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.64 |  | 96 |  | 97.7 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.7 | 14.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC6 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMC1500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-29 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMC1500_11192013164917_9757268
2195048 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1500VA 2U LCD 120V | SMC1500-2U | APC Smart-UPS C 1500VA 2U LCD 120V,SMC1500-2U,; APC Smart-UPS C 1500VA 2U LCD 120V,SMC1500-2UQ,; APC Smart-UPS C 1500VA 2U LCD 120V,SMC1500-2UW, | Ac-output UPS | Static | SMC1500-2U | 900 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 475 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.3 |  | 96.1 |  | 97.6 |  | 97.9 |  | 98 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.8 | 18.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC132 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMC1500-2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-12-01 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMC1500-2U_11192013165025_9825078
2195050 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1000VA LCD RM 2U 120V | SMT1000RM2U | APC Smart-UPS 1000VA LCD RM 2U 120V,SMT1000RM2U,; APC Smart-UPS 1000VA LCD RM 2U 120V,SMT1000RM2UQ,; APC Smart-UPS 1000VA LCD RM 2U 120V,SMT1000RM2UW, | Ac-output UPS | Static | SMT1000RM2U | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.24 |  | 95.2 |  | 97.3 |  | 97.9 |  | 98 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8.7 | 31.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC132 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1000RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-12-01 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1000RM2U_11192013174438_3078035
2195051 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1000VA LCD 120V | SMT1000US | APC Smart-UPS 1000VA LCD 120V,SMT1000US,; APC Smart-UPS 1000VA LCD 120V,SMT1000USQ,; APC Smart-UPS 1000VA LCD 120V,SMT1000USW, | Ac-output UPS | Static | SMT1000 | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.9 |  | 95.4 |  | 97.4 |  | 98 |  | 98.2 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 19 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC6 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1000 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-30 | 2013-01-15 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1000US_11192013174544_3144836
2195053 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD 120V | SMT1500 | ,SMT1500X413,; APC Smart-UPS 1500VA LCD 120V,SMT1500,; APC Smart-UPS 1500VA LCD 120V,SMT1500Q,; APC Smart-UPS 1500VA LCD 120V,SMT1500W, | Ac-output UPS | Static | SMT1500 | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.4 |  | 96.4 |  | 97.8 |  | 98 |  | 98 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.5 | 23.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC7 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-30 | 2012-08-24 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500_11192013174703_3223796
2195054 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1000VA LCD 120V | SMT1000 | APC Smart-UPS 1000VA LCD 120V,SMT1000,; APC Smart-UPS 1000VA LCD 120V,SMT1000Q,; APC Smart-UPS 1000VA LCD 120V,SMT1000QW, | Ac-output UPS | Static | SMT1000 | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 7.9 |  | 95.4 |  | 97.4 |  | 98 |  | 98.2 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 19 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC6 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1000 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-30 | 2012-08-24 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1000_11192013174350_3030304
2195056 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD 120V | SMT1500US | APC Smart-UPS 1500VA LCD 120V,SMT1500US,; APC Smart-UPS 1500VA LCD 120V,SMT1500USQ,; APC Smart-UPS 1500VA LCD 120V,SMT1500USW, | Ac-output UPS | Static | SMT1500 | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.4 |  | 96.4 |  | 97.8 |  | 98 |  | 98 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.5 | 23.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC7 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2009-10-30 | 2013-01-15 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500US_11192013174943_3383667
2195078 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA LCD 120V | SMT2200 | APC Smart-UPS 2200VA LCD 120V,SMT2200,; APC Smart-UPS 2200VA LCD 120V,SMT2200Q,; APC Smart-UPS 2200VA LCD 120V,SMT2200W, | Ac-output UPS | Static | SMT2200 | 1920 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.05 |  | 97.4 |  | 98.2 |  | 98.2 |  | 98.1 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.5 | 22.5 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC55 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT2200 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-01-15 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT2200_11192013211325_5605812
2195080 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA RM 2U LCD 120V | SMT2200RM2U | ,SMT2200R2X106,; APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RM2U,; APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RM2UQ,; APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RM2UW, | Ac-output UPS | Static | SMT2200RM2U | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.86 |  | 97.2 |  | 97.9 |  | 97.8 |  | 97.6 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.1 | 15.2 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT2200RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-11-24 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT2200RM2U_11192013211439_5679558
2195082 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA RM 2U LCD 120V | SMT2200RMUS | APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RMUS,; APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RMUSQ,; APC Smart-UPS 2200VA RM 2U LCD 120V,SMT2200RMUSW, | Ac-output UPS | Static | SMT2200RM2U | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.86 |  | 97.2 |  | 97.9 |  | 97.8 |  | 97.6 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.1 | 15.2 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT2200RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-11-24 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT2200RMUS_11192013211541_5741629
2195084 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA LCD 120V | SMT2200US | APC Smart-UPS 2200VA LCD 120V,SMT2200US,; APC Smart-UPS 2200VA LCD 120V,SMT2200USQ,; APC Smart-UPS 2200VA LCD 120V,SMT2200USW, | Ac-output UPS | Static | SMT2200 | 1920 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.05 |  | 97.4 |  | 98.2 |  | 98.2 |  | 98.1 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.5 | 22.5 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC55 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT2200 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-01-15 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT2200US_11192013212005_6005248
2195088 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA LCD 120V | SMT3000 | APC Smart-UPS 3000VA LCD 120V,SMT3000,; APC Smart-UPS 3000VA LCD 120V,SMT3000Q,; APC Smart-UPS 3000VA LCD 120V,SMT3000W, | Ac-output UPS | Static | SMT3000 | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.39 |  | 98 |  | 98.4 |  | 98.3 |  | 98 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 4.1 | 15.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC55 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT3000 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-01-15 | 2013-04-23 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT3000_11192013213727_7047748
2195090 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA RM 2U LCD 120V | SMT3000RM2U | APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RM2U,; APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RM2UQ,; APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RM2UW, | Ac-output UPS | Static | SMT3000RM2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.93 |  | 97.9 |  | 98.5 |  | 98.4 |  | 98.2 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | SMT3000RM2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT3000RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2010-11-24 | 2012-12-24 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT3000RM2U_11192013213835_7115853
2195092 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA RM 2U LCD 208V | SMT3000RMT2U | APC Smart-UPS 3000VA RM 2U LCD 208V,SMT3000RMT2U,; APC Smart-UPS 3000VA RM 2U LCD 208V,SMT3000RMT2UQ,; APC Smart-UPS 3000VA RM 2U LCD 208V,SMT3000RMT2UW, | Ac-output UPS | Static | SMT3000RMT2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 208-208 | 50-60 | 208-208 | 50-60 | Yes | 2 | 86 | 480 | 690 | 2 | 2 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 208 | 60 | 208 | 60 | 12.37 |  | 97.9 |  | 98.6 |  | 98.6 |  | 98.6 |  | 98.6 | [8 empty] | 1 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT3000RMT2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-10-04 | 2013-02-06 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT3000RMT2U_11192013213933_7173464
2195094 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA RM 2U LCD 120V | SMT3000RMUS | APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RMUS,; APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RMUSQ,; APC Smart-UPS 3000VA RM 2U LCD 120V,SMT3000RMUSW, | Ac-output UPS | Static | SMT3000RM2U | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.93 |  | 97.9 |  | 98.5 |  | 98.4 |  | 98.2 |  | 98.4 | [8 empty] | 0.99 | [22 empty] | 98.4 | SMT3000RM2U | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT3000RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2012-11-24 | 2013-01-11 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT3000RMUS_11192013214033_7233146
2195145 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250-X676 |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250-X676_11202013162740_4860953
2195147 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D_11202013162054_4454425
2195149 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250D-NB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D-NB_11202013162421_4661534
2195151 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PD_11202013162209_4529652
2195153 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250DL-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PDNB_11202013162311_4591307
2195155 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PD_11202013163234_5154750
2195157 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY125K250DR-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PDNB_11202013163313_5193924
2195166 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500-X676 |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500-X676_11202013171346_7626479
2195168 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D_11202013170324_7004115
2195170 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500D-NB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D-NB_11202013170908_7348753
2195172 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PD_11202013170514_7114203
2195173 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500DL-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PDNB_11202013170711_7231978
2195175 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PD_11202013171031_7431836
2195177 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY125K500DR-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PDNB_11202013171135_7495206
2195184 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY150K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250D_11202013184916_3356696
2195186 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY150K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DL-PD_11202013185036_3436545
2195188 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY150K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DR-PD_11202013185226_3546842
2195190 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY200K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250D_11202013192331_5411133
2195192 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY200K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DL-PD_11202013192553_5553962
2195194 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY200K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DR-PD_11202013192519_5519306
2195197 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY250K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500D_11202013194215_6535297
2195199 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY250K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DL-PD_11202013194302_6582895
2195201 | Schneider Electric | APC by Schneider Electric | Symmetra PX250 | SY250K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DR-PD_11202013194350_6630711
2195203 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY300K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500D_11202013200928_8168280
2195205 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY300K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DL-PD_11202013201018_8218304
2195206 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY300K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DR-PD_11202013201120_8280158
2195209 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY400K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500D_11202013203003_9403001
2195211 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY400K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DL-PD_11202013203052_9452778
2195213 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY400K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DR-PD_11202013203144_9504191
2195215 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY500K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500D_11202013204720_0440863
2195217 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY500K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DL-PD_11202013204811_0491042
2195219 | Schneider Electric | APC by Schneider Electric | Symmetra PX500 | SY500K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DR-PD_11202013204859_0539853
2205709 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Rack/Tower LCD 100-127V | SMX2000LV |  | Ac-output UPS | Static | SMX2000LV | 1920 | 1800 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 4 | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.49 |  | 96.1 |  | 97.7 |  | 97.8 |  | 97.9 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 11 | 27.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC143 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX2000LV | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX2000LV_03072014121854_4734765
2205710 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Rack/Tower LCD 100-127V with Network Card | SMX2000LVNC |  | Ac-output UPS | Static | SMX2000LVNC | 1920 | 1800 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 4 | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.83 |  | 95.8 |  | 97.5 |  | 97.7 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 11 | 27.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC143 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX2000LVNC | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX2000LVNC_03072014120124_3684949
2205711 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Rack/Tower LCD 100-127V | SMX2000RMLV2U |  | Ac-output UPS | Static | SMX2000RMLV2U | 1800 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.38 |  | 96.1 |  | 97.7 |  | 97.7 |  | 97.9 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 11 | 27.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC117 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX2000RMLV2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX2000RMLV2U_03072014122126_4886408
2205712 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Rack/Tower LCD 100-127V with Network Card | SMX2000RMLV2UNC |  | Ac-output UPS | Static | SMX2000RMLV2UNC | 1800 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.76 |  | 95.9 |  | 97.5 |  | 97.7 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 11 | 27.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC117 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX2000RMLV2UNC | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX2000RMLV2UNC_03072014120301_3781712
2205713 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2200VA Rack/Tower LCD 100-127V | SMX2200RMLV2U |  | Ac-output UPS | Static | SMX2200RMLV2U | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 667 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.39 |  | 96.5 |  | 97.9 |  | 98 |  | 98.1 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 9.8 | 25.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC117 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX2200RMLV2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX2200RMLV2U_03072014122223_4943604
2205714 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Short Depth Tower/Rack Convertible LCD 208V | SMX3000HVT |  | Ac-output UPS | Static | SMX3000HVT | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 208-208 | 50-60 | 208-208 | 50-60 | Yes | 4 | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 208 | 60 | 208 | 60 | 12.64 |  | 97.9 |  | 97.7 |  | 98 |  | 98.2 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.3 | 18 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC143 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX3000HVT | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX3000HVT_03072014120157_3717589
2205715 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V | SMX3000LV | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V,SMX3000LV,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V,SMX3000LVQ,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V,SMX3000LVQW, | Ac-output UPS | Static | SMX3000LV | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 4 | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.38 |  | 97.3 |  | 98.1 |  | 98.1 |  | 98 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.3 | 18 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC143 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX3000LV | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX3000LV_03072014122030_4830619
2205716 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card | SMX3000LVNC | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,, | Ac-output UPS | Static | SMX3000LVNC | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 4 | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.76 |  | 97.1 |  | 98.1 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.3 | 18 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC143 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX3000LVNC | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX3000LVNC_03072014120221_3741033
2205717 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V | SMX3000RMLV2U |  | Ac-output UPS | Static | SMX3000RMLV2U | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.45 |  | 97.2 |  | 98.2 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.3 | 18 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC117 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX3000RMLV2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX3000RMLV2U_03072014122244_4964146
2205718 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card | SMX3000RMLV2UNC | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,,; APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V with Network Card,, | Ac-output UPS | Static | SMX3000RMLV2UNC | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.96 |  | 97 |  | 98.1 |  | 98.1 |  | 98 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.3 | 18 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC117 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMX3000RMLV2UNC | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-04-01 | 2014-03-05 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMX3000RMLV2UNC_03072014120344_3824833
2205865 | Schneider Electric | APC by Schneider Electric | Smart-UPS 1500VA LCD 120V | DLT1500 | Smart-UPS 1500VA LCD 120V,DLT1500, | Ac-output UPS | Static | SMT1500 | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.39 |  | 96.4 |  | 97.8 |  | 98 |  | 98.1 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 6.5 | 23.1 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC7 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | https://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=DLT1500 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-03-01 | 2014-03-07 | United States, Canada | ES_22220_DLT1500_03102014203703_3823906
2205866 | Schneider Electric | APC by Schneider Electric | Smart-UPS 1500VA LCD RM 2U 120V | DLT1500RM2U |  | Ac-output UPS | Static | SMT1500RM2U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.88 |  | 96.2 |  | 97.7 |  | 97.7 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.2 | 25.8 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC133 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | https://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=DLT1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-03-01 | 2014-03-07 | United States, Canada | ES_22220_DLT1500RM2U_03102014210440_5480746
2205867 | Schneider Electric | APC by Schneider Electric | Smart-UPS 2200VA LCD 120V | DLT2200 | Smart-UPS 2200VA LCD 120V,DLT2200, | Ac-output UPS | Static | SMT2200 | 1920 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.06 |  | 97.5 |  | 98.3 |  | 98.2 |  | 98.2 |  | 98.3 | [8 empty] | 0.99 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.5 | 22.5 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC55 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | https://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=DLT2200 | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-03-01 | 2014-03-07 | United States, Canada | ES_22220_DLT2200_03102014213257_7177579
2205868 | Schneider Electric | APC by Schneider Electric | Smart-UPS 3000VA LCD RM 2U 120V | DLT3000RM2U | Smart-UPS 3000VA LCD RM 2U 120V,DLT3000RM2U, | Ac-output UPS | Static | SMT3000RM2U | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.93 |  | 98 |  | 98.6 |  | 98.4 |  | 98.2 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.4 | 11.7 | 3 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | https://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=DLT3000RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2014-03-01 | 2014-03-07 | United States, Canada | ES_22220_DLT3000RM2U_03102014214436_7876008
2229504 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA RM 208/230V HW | SRT5KRMXLW-HW | APC Smart-UPS SRT 5000VA RM 208/230V HW,SRT5KRMXLW-HW,; APC Smart-UPS SRT 5000VA RM 208/230V HW,SRT5KRMXLW-HWQ,; APC Smart-UPS SRT 5000VA RM 208/230V HW,SRT5KRMXLW-HWW, | Ac-output UPS | Static | SRT5KRMXLW-HW | 4500 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 3 | 130 | 432 | 719 | 0 | 0 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 62.76 | 46.38 | 91.9 | 95.9 | 93.8 | 97.8 | 93.9 | 98.4 | 93.8 | 98.7 | 93.9 | 98.3 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | Other,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT5KRMXLW-HW | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2014-12-16 | United States, Canada | ES_22220_SRT5KRMXLW-HW_12162014225549_0549893
2229506 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA RM 208V | SRT5KRMXLT | APC Smart-UPS SRT 5000VA RM 208V,SRT5KRMXLTQ,; APC Smart-UPS SRT 5000VA RM 208V,SRT5KRMXLTW, | Ac-output UPS | Static | SRT5KRMXLT | 4800 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-208 | 50-60 | 208-240 | 50-60 | Yes | 3 | 130 | 432 | 719 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 65.06 | 48.35 | 91.9 | 95.9 | 93.6 | 97.6 | 93.5 | 98.1 | 93.2 | 98.2 | 93.5 | 98 | [7 empty] | 1 | 1 | [21 empty] | 93.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT5KRMXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2017-05-12 | United States, Canada | ES_22220_SRT5KRMXLT_12172014004941_7381628
2229507 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA RM 208V IEC | SRT5KRMXLT-IEC | APC Smart-UPS SRT 5000VA RM 208V IEC Factory Serviced,SRT5KRMXLT-IECW,; Std ExchAPC Smart-UPS SRT 5000VA RM 208V IEC,SRT5KRMXLT-IECQ, | Ac-output UPS | Static | SRT5KXLT-IEC | 4800 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 3 | 130 | 432 | 719 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 67.76 | 51.23 | 91.6 | 95.6 | 93.4 | 97.4 | 93.3 | 97.9 | 93 | 98 | 93.2 | 97.8 | [7 empty] | 1 | 1 | [21 empty] | 93.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT5KRMXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2018-02-01 | 2014-12-16 | United States, Canada | ES_22220_SRT5KRMXLT-IEC_12172014005240_7560537
2229508 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA 208V | SRT5KXLT | APC Smart-UPS SRT 5000VA 208V,SRT5KXLTQ,; APC Smart-UPS SRT 5000VA 208V,SRT5KXLTW,; Dell Smart-UPS SRT 5000VA 208V,DLRT5KRMXLT, | Ac-output UPS | Static | SRT5KRMXLT | 4800 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 130 | 719 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 65.06 | 48.35 | 91.9 | 95.9 | 93.6 | 97.6 | 93.5 | 98.1 | 93.2 | 98.2 | 93.5 | 98 | [7 empty] | 1 | 1 | [21 empty] | 93.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT5KXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2017-05-15 | United States, Canada | ES_22220_SRT5KXLT_12172014004530_7130335
2229509 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA 208V IEC | SRT5KXLT-IEC | APC Smart-UPS SRT 5000VA 208V IEC Factory Serviced,SRT5KXLT-IECW,; Std ExchAPC Smart-UPS SRT 5000VA 208V IEC,SRT5KXLT-IECQ, | Ac-output UPS | Static | SRT5KXLT-IEC | 4800 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 130 | 719 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 67.76 | 51.23 | 91.6 | 95.6 | 93.4 | 97.4 | 93.3 | 97.9 | 93 | 98 | 93.2 | 97.8 | [7 empty] | 1 | 1 | [21 empty] | 93.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2018-02-01 | 2014-12-16 | United States, Canada | ES_22220_SRT5KXLT-IEC_12172014005138_7498530
2229510 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 6000VA RM 208V | SRT6KRMXLT | APC Smart-UPS SRT 6000VA RM 208V,SRT6KRMXLT,; APC Smart-UPS SRT 6000VA RM 208V,SRT6KRMXLTQ,; APC Smart-UPS SRT 6000VA RM 208V,SRT6KRMXLTW, | Ac-output UPS | Static | SRT6KXLT | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 4 | 174 | 432 | 719 | 5 | 5 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 68.7 | 52.79 | 92.7 | 96.5 | 94.1 | 98.2 | 94 | 98.7 | 93.7 | 98.9 | 93.9 | 98.6 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 8.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT6KRMXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2014-12-16 | United States, Canada | ES_22220_SRT6KRMXLT_12172014010044_8044212
2229511 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 6000VA RM 208V IEC | SRT6KRMXLT-IEC | APC Smart-UPS SRT 6000VA RM 208V IEC,SRT6KRMXLT-IEC,; APC Smart-UPS SRT 6000VA RM 208V IEC,SRT6KRMXLT-IECQ,; APC Smart-UPS SRT 6000VA RM 208V IEC,SRT6KRMXLT-IECW, | Ac-output UPS | Static | SRT6KXLT | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 4 | 174 | 432 | 719 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 68.7 | 52.79 | 92.7 | 96.5 | 94.1 | 98.2 | 94 | 98.7 | 93.7 | 98.9 | 93.9 | 98.6 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 8.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT6KRMXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2014-12-16 | United States, Canada | ES_22220_SRT6KRMXLT-IEC_12172014010226_8146822
2229512 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 6000VA 208V | SRT6KXLT | APC Smart-UPS SRT 6000VA 208V,SRT6KXLT,; APC Smart-UPS SRT 6000VA 208V,SRT6KXLTQ,; APC Smart-UPS SRT 6000VA 208V,SRT6KXLTW, | Ac-output UPS | Static | SRT6KXLT | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 174 | 719 | 5 | 5 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 68.7 | 52.79 | 92.7 | 96.5 | 94.1 | 98.2 | 94 | 98.7 | 93.7 | 98.9 | 93.9 | 98.6 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 8.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT6KXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2014-12-16 | United States, Canada | ES_22220_SRT6KXLT_12172014005955_7995439
2229513 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 6000VA 208V IEC | SRT6KXLT-IEC | APC Smart-UPS SRT 6000VA 208V IEC,SRT6KXLT-IEC,; APC Smart-UPS SRT 6000VA 208V IEC,SRT6KXLT-IECQ,; APC Smart-UPS SRT 6000VA 208V IEC,SRT6KXLT-IECW, | Ac-output UPS | Static | SRT6KXLT | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 174 | 719 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 68.7 | 52.79 | 92.7 | 96.5 | 94.1 | 98.2 | 94 | 98.7 | 93.7 | 98.9 | 93.9 | 98.6 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 8.3 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT6KXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2014-12-15 | 2014-12-16 | United States, Canada | ES_22220_SRT6KXLT-IEC_12172014010129_8089334
2229574 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 10000VA RM 208V | SRT10KRMXLT | APC Smart-UPS SRT 10000VA RM 208V,SRT10KRMXLTQ,; APC Smart-UPS SRT 10000VA RM 208V,SRT10KRMXLTW, | Ac-output UPS | Static | SRT10KRMXLT | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 6 | 263 | 432 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 90.91 | 72 | 93.5 | 97 | 94.5 | 98.4 | 94.3 | 98.8 | 93.8 | 99 | 94.2 | 98.7 | [7 empty] | 1 | 1 | [21 empty] | 94.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 11.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT10KRMXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT10KRMXLT_12182014134543_0343228
2229575 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 10000VA RM 208V IEC | SRT10KRMXLT-IEC | APC Smart-UPS SRT 10000VA RM 208V IEC,SRT10KRMXLT-IECQ,; APC Smart-UPS SRT 10000VA RM 208V IEC,SRT10KRMXLT-IECW, | Ac-output UPS | Static | SRT10KRMXLT | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 6 | 263 | 432 | 715 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 90.91 | 72 | 93.5 | 97 | 94.5 | 98.4 | 94.3 | 98.8 | 93.8 | 99 | 94.2 | 98.7 | [7 empty] | 1 | 1 | [21 empty] | 94.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 11.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT10KRMXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT10KRMXLT-IEC_12182014134620_0380481
2229576 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 10000VA 208V | SRT10KXLT | APC Smart-UPS SRT 10000VA 208V,SRT10KXLTQ,; APC Smart-UPS SRT 10000VA 208V,SRT10KXLTW, | Ac-output UPS | Static | SRT10KRMXLT | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 263 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 90.91 | 72 | 93.5 | 97 | 94.5 | 98.4 | 94.3 | 98.8 | 93.8 | 99 | 94.2 | 98.7 | [7 empty] | 1 | 1 | [21 empty] | 94.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 11.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT10KXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT10KXLT_12182014134425_0265427
2229577 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 10000VA 208V IEC | SRT10KXLT-IEC | APC Smart-UPS SRT 10000VA 208V IEC,SRT10KXLT-IECQ,; APC Smart-UPS SRT 10000VA 208V IEC,SRT10KXLT-IECW, | Ac-output UPS | Static | SRT10KRMXLT | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 263 | 715 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 90.91 | 72 | 93.5 | 97 | 94.5 | 98.4 | 94.3 | 98.8 | 93.8 | 99 | 94.2 | 98.7 | [7 empty] | 1 | 1 | [21 empty] | 94.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 11.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT10KXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT10KXLT-IEC_12182014134500_0300883
2229578 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 8000VA RM 208V | SRT8KRMXLT | APC Smart-UPS SRT 8000VA RM 208V,SRT8KRMXLTQ,; APC Smart-UPS SRT 8000VA RM 208V,SRT8KRMXLTW, | Ac-output UPS | Static | SRT8KRMXLT | 8000 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 6 | 263 | 432 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 92.92 | 72.39 | 92.8 | 96.3 | 94.3 | 98.1 | 94.4 | 98.6 | 94.1 | 98.8 | 94.3 | 98.5 | [7 empty] | 1 | 1 | [21 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.2 | 14.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT8KRMXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT8KRMXLT_12182014133546_9746334
2229579 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 8000VA RM 208V IEC | SRT8KRMXLT-IEC | APC Smart-UPS SRT 8000VA RM 208V IEC,SRT8KRMXLT-IECQ,; APC Smart-UPS SRT 8000VA RM 208V IEC,SRT8KRMXLT-IECW, | Ac-output UPS | Static | SRT8KRMXLT | 8000 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 6 | 263 | 432 | 715 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 92.92 | 72.39 | 92.8 | 96.3 | 94.3 | 98.1 | 94.4 | 98.6 | 94.1 | 98.8 | 94.3 | 98.5 | [7 empty] | 1 | 1 | [21 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.2 | 14.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT8KRMXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT8KRMXLT-IEC_12182014133726_9846640
2229580 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 8000VA 208V | SRT8KXLT | APC Smart-UPS SRT 8000VA 208V,SRT8KXLTQ,; APC Smart-UPS SRT 8000VA 208V,SRT8KXLTW,; Dell Smart-UPS SRT 8000VA 208V,DLRT8KRMXLT, | Ac-output UPS | Static | SRT8KRMXLT | 8000 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 263 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 92.92 | 72.39 | 92.8 | 96.3 | 94.3 | 98.1 | 94.4 | 98.6 | 94.1 | 98.8 | 94.3 | 98.5 | [7 empty] | 1 | 1 | [21 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.2 | 14.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT8KXLT | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT8KXLT_12182014133139_9499690
2229581 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 8000VA 208V IEC | SRT8KXLT-IEC | APC Smart-UPS SRT 8000VA 208V IEC,SRT8KXLT-IECQ,; APC Smart-UPS SRT 8000VA 208V IEC,SRT8KXLT-IECW, | Ac-output UPS | Static | SRT8KRMXLT | 8000 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 263 | 715 | 10 | 10 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 92.92 | 72.39 | 92.8 | 96.3 | 94.3 | 98.1 | 94.4 | 98.6 | 94.1 | 98.8 | 94.3 | 98.5 | [7 empty] | 1 | 1 | [21 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.2 | 14.4 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SRT8KXLT-IEC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-01-02 | 2014-12-18 | United States, Canada | ES_22220_SRT8KXLT-IEC_12182014133403_9643835
2243356 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD 120V | SMT1500X448 |  | Ac-output UPS | Static | SMT1500X448 | 1000 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 9.69 |  | 95.9 |  | 97.5 |  | 97.8 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.5 | 23.1 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC7 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SMT1500X448 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2012-08-31 | 2015-07-15 | United States, Canada | ES_22220_SMT1500X448_07152015195434_0074706
2243357 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V with AP9630 | SMT1500R2X180 |  | Ac-output UPS | Static | SMT1500R2X180 | 1000 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 10.17 |  | 95.8 |  | 97.4 |  | 97.5 |  | 97.7 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7.2 | 25.9 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC133 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SMT1500R2X180 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2012-08-31 | 2015-07-15 | United States, Canada | ES_22220_SMT1500R2X180_07152015202630_1990906
2243359 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA LCD RM 2U 120V with AP9630 | SMT2200R2X180 |  | Ac-output UPS | Static | SMT2200R2X180 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 13.71 |  | 96.8 |  | 97.9 |  | 97.6 |  | 97.6 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.4 | 15.9 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SMT2200R2X180 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2012-08-31 | 2015-07-15 | United States, Canada | ES_22220_SMT2200R2X180_07152015203750_2670387
2243363 | Schneider Electric | APC by Schneider Electric | APC Smart UPS 3000VA LCD RM 2U 120V with 12FT CORD | SMT3000R2X145 |  | Ac-output UPS | Static | SMT3000R2X180 | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.16 |  | 97.9 |  | 98.3 |  | 97.8 |  | 97.5 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SMT3000R2X145 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2012-08-31 | 2015-07-15 | United States, Canada | ES_22220_SMT3000R2X145_07152015204748_3268717
2243364 | Schneider Electric | APC by Schneider Electric | APC Smart-Ups 3000VA LCD RM 2U 120V | SMT3000R2X180 |  | Ac-output UPS | Static | SMT3000R2X180 | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 13.02 |  | 97.7 |  | 98.2 |  | 97.9 |  | 97.6 |  | 97.9 | [8 empty] | 1 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=RBC43 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SMT3000R2X180 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2012-08-31 | 2015-07-15 | United States, Canada | ES_22220_SMT3000R2X180_07152015205943_3983698
2260079 | Schneider Electric | APC by Schneider Electric | BE600M1 | BE600M1 | APC Back-UPS ES 600VA 120V 1 USB charging port Factory Serviced,BE600M1W,; Std Exch APC Back-UPS ES 600VA 120V 1 USB charging port,BE600M1Q, | Ac-output UPS | Static | BE600M1 | 330 | 600 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 274 | 105 | 7 | 5 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.46 |  | 97.1 |  | 98.3 |  | 98.7 |  | 98.8 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 3.2 | 11.6 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC154 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BE600M1 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-06-10 | 2016-05-23 | United States, Canada | ES_22220_BE600M1_02052016070508_5908354
2260082 | Schneider Electric | APC by Schneider Electric | APC Back-UPS NS 650VA 120V 1 USB charging port Retail | BN650M1 | APC Back-UPS NS 650VA 120V 1 USB charging port Retail Factory Serviced,BN650M1W,; Std Exch APC Back-UPS NS 650VA 120V 1 USB charging port Retail,BN650M1Q, | Ac-output UPS | Static | BN650M1 | 360 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 274 | 105 | 7 | 5 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.48 |  | 97.3 |  | 98.4 |  | 98.8 |  | 98.8 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.5 | 10.2 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC154 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BN650M1 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-02-24 | 2016-03-24 | United States | ES_22220_BN650M1_02052016072148_6908273
2260083 | Schneider Electric | APC by Schneider Electric | APC Back-UPS NS 650VA 120V 1 USB charging port Retail Canada | BN650M1-CA | APC Back-UPS NS 650VA 120V 1 USB charging port Retail Canada Factory Serviced,BN650M1-CAW,; Std Exch APC Back-UPS NS 650VA 120V 1 USB charging port Retail Canada,BN650M1-CAQ, | Ac-output UPS | Static | BN650M1 | 360 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 274 | 105 | 7 | 5 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.48 |  | 97.3 |  | 98.4 |  | 98.8 |  | 98.8 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.5 | 10.2 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC154 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BN650M1-CA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-04-21 | 2016-03-24 | Canada | ES_22220_BN650M1-CA_02052016073120_7480763
2260104 | Schneider Electric | APC by Schneider Electric | Galaxy VM 160 kVA UPS Single 480-480 V, 65kAIC, Start up 5x8 | GVMRB160KG65S |  | Ac-output UPS | Static | GVMPB160KGS | 144000 | 160000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1072 | 523 | 95.1 | 98.1 | 96.4 | 99 | 96.5 | 99.2 | 96.4 | 99.3 | 96.1 | 99 | [7 empty] | 1 | 1 | [21 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMRB160KG65S_02022016003820_3500871
2260106 | Schneider Electric | APC by Schneider Electric | Symmetra PX 10kW Scalable to 100kW 208V with Startup | SY10K100F | Symmetra PX 10kW Scalable to 100kW 208V with Startup No Battery,SY10K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY10K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY10K100F_01282016181834_5114322
2260107 | Schneider Electric | APC by Schneider Electric | Symmetra PX 30kW Scalable to 100kW 208V with Startup | SY30K100F | Symmetra PX 30kW Scalable to 100kW 208V with Startup No Battery,SY30K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY30K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY30K100F_01282016182522_5522643
2260108 | Schneider Electric | APC by Schneider Electric | Symmetra PX 40kW Scalable to 100kW 208V with Startup | SY40K100F | Symmetra PX 40kW Scalable to 100kW 208V with Startup No Battery,SY40K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY40K100F_01282016182726_5646406
2260109 | Schneider Electric | APC by Schneider Electric | Symmetra PX 50kW Scalable to 100kW 208V with Startup | SY50K100F | Symmetra PX 50kW Scalable to 100kW 208V with Startup No Battery,SY50K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY50K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY50K100F_01282016182847_5727636
2260110 | Schneider Electric | APC by Schneider Electric | Symmetra PX 60kW Scalable to 100kW 208V with Startup | SY60K100F | Symmetra PX 60kW Scalable to 100kW 208V with Startup No Battery,SY60K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY60K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY60K100F_01282016183122_5882364
2260111 | Schneider Electric | APC by Schneider Electric | Symmetra PX 70kW Scalable to 100kW 208V with Startup | SY70K100F | Symmetra PX 70kW Scalable to 100kW 208V with Startup No Battery,SY70K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY70K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY70K100F_01282016183237_5957700
2260112 | Schneider Electric | APC by Schneider Electric | Symmetra PX 80kW Scalable to 100kW 208V with Startup | SY80K100F | Symmetra PX 80kW Scalable to 100kW 208V with Startup No Battery,SY80K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY80K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY80K100F_01282016183859_6339257
2260113 | Schneider Electric | APC by Schneider Electric | Symmetra PX 90kW Scalable to 100kW 208V with Startup | SY90K100F | Symmetra PX 90kW Scalable to 100kW 208V with Startup No Battery,SY90K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY90K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY90K100F_01282016184023_6423222
2260114 | Schneider Electric | APC by Schneider Electric | Symmetra PX 100kW Scalable to 100kW 208V with Startup | SY100K100F | Symmetra PX 100kW Scalable to 100kW 208V with Startup No Battery,SY100K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY100K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY100K100F_01282016184141_6501892
2260115 | Schneider Electric | APC by Schneider Electric | Symmetra PX 20kW Scalable to 100kW 208V with Startup | SY20K100F | Symmetra PX 20kW Scalable to 100kW 208V with Startup No Battery,SY20K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY20K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY20K100F_01282016182335_5415497
2263049 | Schneider Electric | APC by Schneider Electric | APC Back-UPS NS 675VA 1 USB charging port 120V Retail | BN675M1 | APC Back-UPS NS 675VA 1 USB charging port 120V Retail Factory Serviced,BN675M1W,; Std Exch APC Back-UPS NS 675VA 1 USB charging port 120V Retail,BN675M1Q, | Ac-output UPS | Static | BN675M1 | 360 | 675 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 274 | 105 | 7 | 5 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.46 |  | 97.1 |  | 98.4 |  | 98.7 |  | 98.8 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.5 | 10.2 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC154 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BN675M1 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-04-12 | 2016-03-24 | United States, Canada | ES_22220_BN675M1_03242016095642_3402943
2269052 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 2200VA RM 120V | SRT2200RMXLA | APC Smart-UPS SRT 2200VA RM 120V Factory Serviced,SRT2200RMXLAW,; Std Exch APC Smart-UPS SRT 2200VA RM 120V,SRT2200RMXLAQ, | Ac-output UPS | Static | SRT2200RMXLA | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 584 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 45.14 | 34.71 | 87.7 | 92.6 | 91.2 | 95.8 | 91.7 | 96.8 | 91.9 | 97.2 | 91.6 | 96.6 | [7 empty] | 0.99 | 0.99 | [21 empty] | 91.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.7 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC141 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT2200RMXLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT2200RMXLA_06062016182721_7641491
2269053 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 2200VA 120V | SRT2200XLA | APC Smart-UPS SRT 2200VA 120V Factory Serviced,SRT2200XLAW,; Std Exch APC Smart-UPS SRT 2200VA 120V,SRT2200XLAQ, | Ac-output UPS | Static | SRT2200RMXLA | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 85 | 584 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 45.14 | 34.71 | 87.7 | 92.6 | 91.2 | 95.8 | 91.7 | 96.8 | 91.9 | 97.2 | 91.6 | 96.6 | [7 empty] | 0.99 | 0.99 | [21 empty] | 91.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.7 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC141 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT2200XLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT2200XLA_06062016183142_7902717
2269060 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 2200VA RM 120V Network Card | SRT2200RMXLA-NC | ,SRT2200RXLANCQ,; ,SRT2200RXLANCW, | Ac-output UPS | Static | SRT2200RMXLA-NC | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 584 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.82 | 36.26 | 87.4 | 92.3 | 91.1 | 95.7 | 91.6 | 96.7 | 91.8 | 97.1 | 91.5 | 96.5 | [7 empty] | 0.99 | 0.99 | [21 empty] | 91.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.7 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC141 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT2200RMXLA-NC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT2200RMXLA-NC_06062016195451_2891418
2269065 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA RM 120V | SRT3000RMXLA | APC Smart-UPS SRT 3000VA RM 120V Factory Serviced,SRT3000RMXLAW,; Std Exch APC Smart-UPS SRT 3000VA RM 120V,SRT3000RMXLAQ, | Ac-output UPS | Static | SRT3000RMXLA | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 635 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 47.72 | 37.54 | 89.4 | 94.4 | 91.9 | 96.8 | 91.9 | 97.4 | 91.7 | 97.5 | 91.8 | 97.2 | [7 empty] | 0.99 | 1 | [21 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT3000RMXLA_06062016202406_4646142
2269066 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA 120V | SRT3000XLA | APC Smart-UPS SRT 3000VA 120V Factory Serviced,SRT3000XLAW,; Std Exch APC Smart-UPS SRT 3000VA 120V,SRT3000XLAQ, | Ac-output UPS | Static | SRT3000RMXLA | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 85 | 635 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 47.72 | 37.54 | 89.4 | 94.4 | 91.9 | 96.8 | 91.9 | 97.4 | 91.7 | 97.5 | 91.8 | 97.2 | [7 empty] | 0.99 | 1 | [21 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT3000XLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT3000XLA_06062016203124_5084910
2269067 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA RM 120V Network Card | SRT3000RMXLA-NC | Std Exch APC Smart-UPS SRT 3000VA RM 120V Network Card,SRT3000RXLANCQ,; Std Exch APC Smart-UPS SRT 3000VA RM 120V Network Card,SRT3000RXLANCW, | Ac-output UPS | Static | SRT3000RMXLA-NC | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 635 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 49.6 | 39.24 | 89.2 | 94.2 | 91.8 | 96.7 | 91.9 | 97.3 | 91.7 | 97.5 | 91.8 | 97.2 | [7 empty] | 0.99 | 1 | [21 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLA-NC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-09-03 | 2016-06-06 | United States, Canada | ES_22220_SRT3000RMXLA-NC_06062016204112_5672478
2272082 | Schneider Electric | APC by Schneider Electric | BN900M | BN900M | APC Back-UPS NS 900VA Retail 120V Factory Serviced,BN900MW,; BN900MQ,BN900MQ, | Ac-output UPS | Static | BN900M | 480 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 327 | 105 | 9 | 6 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.44 |  | 97.9 |  | 98.7 |  | 98.9 |  | 98.9 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.2 | 9.6 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC17 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BN900M | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-07-15 | 2016-05-23 | United States | ES_22220_BN900M_07112016083322_6002334
2272083 | Schneider Electric | APC by Schneider Electric | BN900M-CA | BN900M-CA | APC Back-UPS NS 900VA Retail Canada 120V Factory Serviced,BN900M-CAW,; BN900M-CAQ,BN900M-CAQ, | Ac-output UPS | Static | BN900M | 480 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 327 | 105 | 9 | 6 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.44 |  | 97.9 |  | 98.7 |  | 98.9 |  | 98.9 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.2 | 9.6 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC17 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BN900M-CA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-08-12 | 2016-05-23 | Canada | ES_22220_BN900M-CA_07112016083539_6139596
2272084 | Schneider Electric | APC by Schneider Electric | BE850M2 | BE850M2 | APC Back-UPS ES 850VA 2 USB charging ports 120V Factory Serviced,BE850M2W,; Std Exch APC Back-UPS ES 850VA 2 USB charging ports 120V,BE850M2Q, | Ac-output UPS | Static | BE850M2 | 450 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 139 | 327 | 105 | 9 | 6 | 3 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.04 |  | 97.2 |  | 98.4 |  | 98.7 |  | 98.7 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.7 | 10.7 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC17 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-BE850M2 | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2016-08-12 | 2016-05-23 | United States, Canada | ES_22220_BE850M2_07112016084347_6627861
2280005 | Schneider Electric | APC by Schneider Electric | BN450M | BN450M | APC Back-UPS NS 6 Outlet 450VA 120V Retail Factory Serviced,BN450MW,; Std Exch APC Back-UPS NS 6 Outlet 450VA 120V Retail,BN450MQ, | Ac-output UPS | Static | BN450M | 255 | 450 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 140 | 253 | 105 | 6 | 4 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.73 |  | 95.8 |  | 97.8 |  | 98.4 |  | 98.6 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.6 | 5.2 | 3 | N/A | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | None | None |  | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN450M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2016-08-30 | 2016-05-23 | United States | ES_22220_BN450M_09212016083810_7090394
2280006 | Schneider Electric | APC by Schneider Electric | BN450M-CA | BN450M-CA | APC Back-UPS NS 6 Outlet 450VA 120V Retail Canada Factory Serviced,BN450M-CAW,; Std Exch APC Back-UPS NS 6 Outlet 450VA 120V Retail Canada,BN450M-CAQ, | Ac-output UPS | Static | BN450M | 255 | 450 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 140 | 253 | 105 | 6 | 4 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.73 |  | 95.8 |  | 97.8 |  | 98.4 |  | 98.6 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.6 | 5.2 | 3 | N/A | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | None | None |  | Yes | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/ca/en/products/P-BN450M-CA | http://www.apc.com/ca/en/who-we-are/sustainability/ | 2016-08-30 | 2016-05-23 | Canada | ES_22220_BN450M-CA_09212016085933_8373566
2280007 | Schneider Electric | APC by Schneider Electric | BE425M | BE425M | APC Back-UPS ES 6 Outlet 425VA 120V Factory Serviced,BE425MW,; BE425MQ,BE425MQ, | Ac-output UPS | Static | BN450M | 255 | 425 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 140 | 253 | 105 | 6 | 4 | 2 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.73 |  | 95.8 |  | 97.8 |  | 98.4 |  | 98.6 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2.6 | 5.2 | 3 | N/A | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | None | None |  | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BE425M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2016-08-30 | 2016-05-23 | United States, Canada | ES_22220_BE425M_09222016093021_6621394
2282457 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA RM 208V | SRT3000RMXLT | APC Smart-UPS SRT 3000VA RM 208V Factory Serviced,SRT3000RMXLTW,; Std Exch APC Smart-UPS SRT 3000VA RM 208V,SRT3000RMXLTQ, | Ac-output UPS | Static | SRT3000RMXLT | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 2 | 85 | 432 | 635 | 3 | 3 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 56.27 | 45.44 | 89.3 | 93.5 | 92.2 | 96.4 | 92.7 | 97.4 | 92.7 | 97.8 | 92.5 | 97.2 | [7 empty] | 0.99 | 0.99 | [21 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLT | http://www.apc.com/us/en/who-we-are/sustainability/ | 2015-10-25 | 2016-10-26 | United States, Canada | ES_22220_SRT3000RMXLT_10262016160213_7733491
2282459 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA 208V | SRT3000XLT | APC Smart-UPS SRT 3000VA 208V Factory Serviced,SRT3000XLTW,; Std Exch APC Smart-UPS SRT 3000VA 208V,SRT3000XLTQ, | Ac-output UPS | Static | SRT3000RMXLT | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 85 | 635 | 3 | 3 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 56.27 | 45.44 | 89.3 | 93.5 | 92.2 | 96.4 | 92.7 | 97.4 | 92.7 | 97.8 | 92.5 | 97.2 | [7 empty] | 0.99 | 0.99 | [21 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SRT3000XLT | http://www.apc.com/us/en/who-we-are/sustainability/ | 2015-10-25 | 2016-10-26 | United States, Canada | ES_22220_SRT3000XLT_10262016160536_7936595
2282466 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA RM 208V Network Card | SRT3000RMXLT-NC | APC Smart-UPS SRT 3000VA RM 208V Network Card Factory Serviced,SRT3000RMXLT-NCW,; Std Exch APC Smart-UPS SRT 3000VA RM 208V Network Card,SRT3000RMXLT-NCQ, | Ac-output UPS | Static | SRT3000RMXLT-NC | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 2 | 85 | 432 | 635 | 3 | 3 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 57.87 | 46.92 | 89.1 | 93.3 | 92.1 | 96.3 | 92.6 | 97.3 | 92.6 | 97.7 | 92.4 | 97.1 | [7 empty] | 0.99 | 0.99 | [21 empty] | 92.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLT-NC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2015-10-25 | 2016-10-26 | United States, Canada | ES_22220_SRT3000RMXLT-NC_10262016162607_9167532
2282469 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V NC | SMT1500RM2UNC | APC Smart-UPS 1500VA LCD RM 2U 120V NC Factory Serviced,SMT1500RM2UNCW,; Std Exch APC Smart-UPS 1500VA LCD RM 2U 120V NC,SMT1500RM2UNCQ, | Ac-output UPS | Static | SMT1500RM2UNC | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 10.09 |  | 95.8 |  | 97.4 |  | 97.6 |  | 97.6 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7.2 | 25.9 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC133 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1500RM2UNC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-01-12 | 2016-10-26 | United States, Canada | ES_22220_SMT1500RM2UNC_10262016170924_1764379
2282470 | Schneider Electric | APC by Schneider Electric | APC SMART-UPS 2200VA LCD RM 2U 120V NC | SMT2200RM2UNC | APC Smart-UPS 2200VA LCD RM 2U 120V NC Factory Serviced,SMT2200RM2UNCW,; Std Exch APC Smart-UPS 2200VA LCD RM 2U 120V NC,SMT2200RM2UNCQ, | Ac-output UPS | Static | SMT2200RM2UNC | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 13.09 |  | 97 |  | 98 |  | 97.7 |  | 97.6 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.4 | 15.9 | 2 | http://www.apc.com/shop/us/en/products/P-RBC43 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,SNMP (v1, 2 or 3),HTTP | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT2200RM2UNC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-01-12 | 2016-10-26 | United States, Canada | ES_22220_SMT2200RM2UNC_10262016171924_2364056
2282471 | Schneider Electric | APC by Schneider Electric | APC SMART-UPS 1500VA LCD 120V NC | SMT1500NC | APC Smart-UPS 1500VA LCD 120V NC Factory Serviced,SMT1500NCW,; Std Exch APC Smart-UPS 1500VA LCD 120V NC,SMT1500NCQ, | Ac-output UPS | Static | SMT1500NC | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 10.05 |  | 95.8 |  | 97.4 |  | 97.6 |  | 97.7 |  | 97.6 | [8 empty] | 0.99 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.5 | 23.1 | 2 | http://www.apc.com/shop/us/en/products/P-RBC7 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1500NC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-01-12 | 2016-10-26 | United States, Canada | ES_22220_SMT1500NC_10262016172719_2839570
2282472 | Schneider Electric | APC by Schneider Electric | APC SMART-UPS 3000VA LCD RM 2U 120V NC | SMT3000RM2UNC | APC Smart-UPS 3000VA LCD RM 2U 120V NC Factory Serviced,SMT3000RM2UNCW,; Std Exch APC Smart-UPS 3000VA LCD RM 2U 120V NC,SMT3000RM2UNCQ, | Ac-output UPS | Static | SMT3000RM2UNC | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 13.48 |  | 97.6 |  | 98.1 |  | 97.8 |  | 97.5 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.4 | 11.7 | 2 | http://www.apc.com/shop/us/en/products/P-RBC43 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT3000RM2UNC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-01-12 | 2016-10-26 | United States, Canada | ES_22220_SMT3000RM2UNC_10262016174417_3857945
2286534 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1000VA LCD RM 2U 120V with SmartConnect | SMC1000-2UC | APC Smart-UPS C 1000VA LCD RM 2U 120V with SmartConnect Factory Serviced,SMC1000-2UCW,; Std Exch APC Smart-UPS C 1000VA LCD RM 2U 120V with SmartConnect,SMC1000-2UCQ, | Ac-output UPS | Static | SMC1000-2UC | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 432 | 406 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.77 |  | 95.6 |  | 97.5 |  | 98.1 |  | 98.3 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 9.2 | 22.5 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC124 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMC1000-2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMC1000-2UC_12202016080121_0881303
2288563 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1000VA 120V with SmartConnect | SMC1000C | ,SMC1000CQ,; ,SMC1000CW, | Ac-output UPS | Static | SMC1000C | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.68 |  | 95.6 |  | 97.5 |  | 98.1 |  | 98.3 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 9.2 | 22.5 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC142 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMC1000C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMC1000C_01162017060409_6649519
2288564 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1500VA RM 2U 120V with SmartConnect | SMC1500-2UC | APC Smart-UPS C 1500VA RM 2U 120V with SmartConnect Factory Serviced,SMC1500-2UCW,; Std Exch APC Smart-UPS C 1500VA RM 2U 120V with SmartConnect,SMC1500-2UCQ, | Ac-output UPS | Static | SMC1500-2UC | 900 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 432 | 477 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.73 |  | 96.9 |  | 98.1 |  | 98.3 |  | 98.3 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 10.1 | 25 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC132 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMC1500-2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMC1500-2UC_01162017062051_7651743
2288565 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS C 1500VA 120V with SmartConnect | SMC1500C | APC Smart-UPS C 1500VA 120V with SmartConnect Factory Serviced,SMC1500CW,; Std Exch APC Smart-UPS C 1500VA 120V with SmartConnect,SMC1500CQ, | Ac-output UPS | Static | SMC1500C | 900 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.71 |  | 96.9 |  | 98.1 |  | 98.3 |  | 98.3 |  | 98.2 | [8 empty] | 1 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7.8 | 20.4 | 2 | http://www.apc.com/shop/us/en/products/P-RBC6 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMC1500C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMC1500C_01162017073244_1964315
2288566 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1000VA LCD RM 2U 120V with SmartConnect | SMT1000RM2UC | APC Smart-UPS 1000VA LCD RM 2U 120V with SmartConnect Factory Serviced,SMT1000RM2UCW,; Std Exch APC Smart-UPS 1000VA LCD RM 2U 120V with SmartConnect,SMT1000RM2UCQ, | Ac-output UPS | Static | SMT1000RM2UC | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 432 | 477 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.74 |  | 96.1 |  | 97.8 |  | 98.2 |  | 98.3 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8.5 | 29.9 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC132 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1000RM2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT1000RM2UC_01162017074501_2701702
2288567 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1000VA LCD 120V with SmartConnect | SMT1000C | APC Smart-UPS 1000VA LCD 120V with SmartConnect Factory Serviced,SMT1000CW,; Std Exch APC Smart-UPS 1000VA LCD 120V with SmartConnect,SMT1000CQ, | Ac-output UPS | Static | SMT1000C | 700 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.72 |  | 96.2 |  | 97.8 |  | 98.3 |  | 98.4 |  | 98.2 | [8 empty] | 0.99 | [22 empty] | 98.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 19.1 | 2 | http://www.apc.com/shop/us/en/products/P-RBC6 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1000C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT1000C_01162017080137_3697580
2288570 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V with SmartConnect | SMT1500RM2UC |  | Ac-output UPS | Static | SMT1500RM2UC | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 432 | 477 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.68 |  | 97.2 |  | 98.2 |  | 98.4 |  | 98.2 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7.2 | 25.9 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC133 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1500RM2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT1500RM2UC_01162017082032_4832827
2288571 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 1500VA LCD 120V with SmartConnect | SMT1500C | APC Smart-UPS 1500VA LCD 120V with SmartConnect Factory Serviced,SMT1500CW,; Std Exch APC Smart-UPS 1500VA LCD 120V with SmartConnect,SMT1500CQ, | Ac-output UPS | Static | SMT1500C | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 219 | 171 | 439 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.7 |  | 97.2 |  | 98.2 |  | 98.4 |  | 98.3 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.5 | 23.1 | 2 | http://www.apc.com/shop/us/en/products/P-RBC7 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT1500C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT1500C_01162017083227_5547872
2288572 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 750VA RM 2U 120V with SmartConnect | SMT750RM2UC | APC Smart-UPS 750VA RM 2U 120V with SmartConnect Factory Serviced,SMT750RM2UCW,; Std Exch APC Smart-UPS 750VA RM 2U 120V with SmartConnect,SMT750RM2UCQ, | Ac-output UPS | Static | SMT750RM2UC | 500 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 86 | 432 | 409 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.73 |  | 94.8 |  | 97.1 |  | 97.8 |  | 98.1 |  | 97.7 | [8 empty] | 0.98 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.5 | 16.1 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC123 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT750RM2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT750RM2UC_01162017084221_6141650
2288573 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 750VA LCD 120V with SmartConnect | SMT750C | APC Smart-UPS 750VA LCD 120V with SmartConnect Factory Serviced,SMT750CW,; Std Exch APC Smart-UPS 750VA LCD 120V with SmartConnect,SMT750CQ, | Ac-output UPS | Static | SMT750C | 500 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 161 | 138 | 369 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 6.32 |  | 95 |  | 97.2 |  | 97.9 |  | 98.1 |  | 97.8 | [8 empty] | 1 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.6 | 15.9 | 2 | http://www.apc.com/shop/us/en/products/P-RBC48 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other | USB Power Sum Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT750C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-03-30 | 2016-12-20 | United States, Canada | ES_22220_SMT750C_01162017093612_9372955
2290699 | Schneider Electric | APC by Schneider Electric | Dell Smart-UPS SRT 3000VA RM 120V | DLRT3000RMXLA | Dell Smart-UPS SRT 3000VA RM 120V Factory Serviced,DLRT3000RMXLAW,; Std Exch Dell Smart-UPS SRT 3000VA RM 120V,DLRT3000RMXLAQ, | Ac-output UPS | Static | SRT3000RMXLA | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 635 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 47.72 |  | 89.4 | 94.4 | 91.9 | 96.8 | 91.9 | 97.4 | 91.7 | 97.5 | 91.8 | 97.2 | [7 empty] | 1 | 1 |  | 47.72 | [19 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-03-01 | 2017-02-15 | United States, Canada | ES_22220_DLRT3000RMXLA_02152017160909_4949916
2291921 | Schneider Electric | APC by Schneider Electric | Back UPS Pro BX 850VA 8 Outlets AVR LCD | BX850M | Back UPS Pro BX 850VA 8 Outlets AVR LCD interface,BX850MW,; Std Exch Back UPS Pro BX 850VA 8 Outlets AVR LCD,BX850MQ, | Ac-output UPS | Static | BX850M | 510 | 850 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 190 | 91 | 310 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.2 |  | 96.7 |  | 98.1 |  | 98.5 |  | 98.7 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 8.9 | 3 | http://www.apc.com/shop/us/en/products/P-RBC17 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BX850M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-02-28 | 2017-03-01 | United States | ES_22220_BX850M_03062017055032_9432194
2291922 | Schneider Electric | APC by Schneider Electric | Back UPS Pro BX 1000VA 8 Outlets AVR LCD | BX1000M | Back UPS Pro BX 1000VA 8 OutletsAVR LCDinterface,BX1000MW,; Std Exch Back UPS Pro BX 1000VA 8 Outlets AVR LCD,BX1000MQ, | Ac-output UPS | Static | BX1000M | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 190 | 91 | 310 | 8 | 4 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.3 |  | 97.1 |  | 98.3 |  | 98.6 |  | 98.7 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 10.6 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC158 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BX1000M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-02-28 | 2017-03-01 | United States | ES_22220_BX1000M_03062017081045_7845247
2291923 | Schneider Electric | APC by Schneider Electric | Back UPS Pro BX 1350VA 10 Outlets AVR LCD | BX1350M | Back UPS Pro BX 1350VA 10 OutletsAVR LCDinterface,BX1350MW,; Std Exch Back UPS Pro BX 1350VA 10 Outlets AVR LCD,BX1350MQ, | Ac-output UPS | Static | BX1350M | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 250 | 100 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.8 |  | 97.5 |  | 98.4 |  | 98.6 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.5 | 10.1 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC123 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BX1350M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-02-28 | 2017-03-01 | United States | ES_22220_BX1350M_03062017082324_8604631
2291925 | Schneider Electric | APC by Schneider Electric | Back UPS Pro BX 1500VA 10 Outlets AVR LCD | BX1500M | Back UPS Pro BX 1500VA 10 OutletsAVR LCDinterface,BX1500MW,; Std Exch Back UPS Pro BX 1500VA 10 Outlets AVR LCD,BX1500MQ, | Ac-output UPS | Static | BX1500M | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 250 | 100 | 382 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 5.3 |  | 97.5 |  | 98.4 |  | 98.6 |  | 98.6 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.8 | 10.9 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC124 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BX1500M | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-02-28 | 2017-03-01 | United States | ES_22220_BX1500M_03062017083802_9482358
2294285 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1000VA RM 120V | SRT1000RMXLA | APC Smart-UPS SRT 1000VA RM 120V Factory Serviced,SRT1000RMXLAW,; Std Exch APC Smart-UPS SRT 1000VA RM 120V,SRT1000RMXLAQ, | Ac-output UPS | Static | SRT1000RMXLA | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 37.78 | 32.32 | 82.9 | 87.3 | 88.6 | 93 | 90.4 | 95.1 | 90.7 | 96.1 | 90 | 93.4 | [7 empty] | 0.99 | 1 | [21 empty] | 90 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 10.5 | 25.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1000RMXLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1000RMXLA_04132017223215_2735008
2294286 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1000VA 120V | SRT1000XLA | APC Smart-UPS SRT 1000VA 120V Factory Serviced,SRT1000XLAW,; Std Exch APC Smart-UPS SRT 1000VA 120V,SRT1000XLAQ, | Ac-output UPS | Static | SRT1000RMXLA | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 85 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 37.78 | 32.32 | 82.9 | 87.3 | 88.6 | 93 | 90.4 | 95.1 | 90.7 | 96.1 | 90 | 93.4 | [7 empty] | 0.99 | 1 | [21 empty] | 90 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 10.5 | 25.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1000XLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1000XLA_04132017223149_2709195
2295148 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1500VA RM 120V | SRT1500RMXLA | APC Smart-UPS SRT 1500VA RM 120V Factory Serviced,SRT1500RMXLAW,; Std Exch APC Smart-UPS SRT 1500VA RM 120V,SRT1500RMXLAQ, | Ac-output UPS | Static | SRT1500XLA | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 38.6 | 32.74 | 86.6 | 91 | 90.4 | 95 | 90.8 | 96.3 | 91 | 96.9 | 90.7 | 95.2 | [7 empty] | 1 | 1 | [21 empty] | 90.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.6 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1500RMXLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1500RMXLA_04292017193523_4523431
2295149 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1500VA 120V | SRT1500XLA | APC Smart-UPS SRT 1500VA 120V Factory Serviced,SRT1500XLAW,; Std Exch APC Smart-UPS SRT 1500VA 120V,SRT1500XLAQ, | Ac-output UPS | Static | SRT1500XLA | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 432 | 85 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 38.6 | 32.74 | 86.6 | 91 | 90.4 | 95 | 90.8 | 96.3 | 91 | 96.9 | 90.7 | 95.2 | [7 empty] | 1 | 1 | [21 empty] | 90.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.6 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1500XLA | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1500XLA_04292017193224_4344599
2295150 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1000VA RM 120V Network Card | SRT1000RMXLA-NC | Std Exch APC Smart-UPS SRT 1000VA RM 120V Network,SRT1000RXLANCQ,; Std Exch APC Smart-UPS SRT 1000VA RM 120V Network,SRT1000RXLANCW, | Ac-output UPS | Static | SRT1000RMXLA-NC | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 39.3 | 33.8 | 82.5 | 86.8 | 88.4 | 92.8 | 90.3 | 94.9 | 90.6 | 95.9 | 89.8 | 93.1 | [7 empty] | 0.99 | 1 | [21 empty] | 89.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 10.5 | 25.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1000RMXLA-NC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1000RMXLA-NC_04292017195832_5912030
2295151 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 1500VA RM 120V Network Card | SRT1500RMXLA-NC | APC Smart-UPS SRT 1500VA RM 120V Network Card Fact,SRT1500RXLANCW,; Std Exch APC Smart-UPS SRT 1500VA RM 120V Network,SRT1500RXLANCQ, | Ac-output UPS | Static | SRT1500RMXLA-NC | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 85 | 432 | 508 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 39.72 | 34.34 | 86.3 | 90.6 | 90.2 | 94.8 | 90.8 | 96.2 | 90.9 | 96.8 | 90.6 | 95 | [7 empty] | 1 | 1 | [21 empty] | 90.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.6 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC155 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3),Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT1500RMXLA-NC | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2017-05-30 | 2017-04-13 | United States, Canada | ES_22220_SRT1500RMXLA-NC_04292017201010_6610362
2306571 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA LCD 120V with SmartConnect | SMT2200C | APC Smart-UPS 2200VA LCD 120V with SmartConnect Factory Serviced,SMT2200CW,; Std Exch APC Smart-UPS 2200VA LCD 120V with SmartConnect,SMT2200CQ, | Ac-output UPS | Static | SMT2200C | 1920 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 110-127 | 50-60 | 110-127 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.54 |  | 97.9 |  | 98.5 |  | 98.3 |  | 98.2 |  | 98.3 | [8 empty] | 1 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8.84 | 26.2 | 2 | http://www.apc.com/shop/us/en/products/P-RBC55 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other,Modbus RTU | USB Pwr Sum SmartConnect | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT2200C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-01 | 2017-11-14 | United States, Canada | ES_22220_SMT2200C_11192017064423_3863076
2306572 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 2200VA LCD RM 2U 120V with SmartConnect | SMT2200RM2UC | APC Smart-UPS 2200VA LCD RM 2U 120V with SmartConnect Factory Serviced,SMT2200RM2UCW,; Std Exch APC Smart-UPS 2200VA LCD RM 2U 120V with SmartConnect,SMT2200RM2UCQ, | Ac-output UPS | Static | SMT2200RM2UC | 1920 | 1920 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 110-127 | 50-60 | 110-127 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  | 8.54 | 98 |  | 98.6 |  | 98.4 |  | 98.3 |  | 98.4 | [8 empty] | 1 | [22 empty] | 98.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.09 | 17.93 | 2 | http://www.apc.com/shop/us/en/products/P-RBC43 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other,Modbus RTU | USB Pwr Sum SmartConnect | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT2200RM2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-01 | 2017-11-14 | United States, Canada | ES_22220_SMT2200RM2UC_11192017065916_4756596
2306573 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA LCD 120V with SmartConnect | SMT3000C | APC Smart-UPS 3000VA LCD 120V with SmartConnect Factory Serviced,SMT3000CW,; Std Exch APC Smart-UPS 3000VA LCD 120V with SmartConnect,SMT3000CQ, | Ac-output UPS | Static | SMT3000C | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 110-127 | 50-60 | 110-127 | 50-60 | No |  | 432 | 196 | 544 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.46 |  | 98.4 |  | 98.7 |  | 98.5 |  | 98.3 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.62 | 17.22 | 2 | http://www.apc.com/shop/us/en/products/P-RBC55 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other,Modbus RTU | USB Pwr Sum SmartConnect | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT3000C | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-01 | 2017-11-14 | United States, Canada | ES_22220_SMT3000C_11192017071357_5637180
2306574 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS 3000VA LCD RM 120V with SmartConnect | SMT3000RM2UC | APC Smart-UPS 3000VA LCD RM 120V with SmartConnect Factory Serviced,SMT3000RM2UCW,; Std Exch APC Smart-UPS 3000VA LCD RM 120V with SmartConnect,SMT3000RM2UCQ, | Ac-output UPS | Static | SMT3000RM2UC | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 110-127 | 50-60 | 110-127 | 50-60 | Yes | 2 | 86 | 480 | 683 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  | 8.5 | 98.4 |  | 98.7 |  | 98.5 |  | 98.2 |  | 98.5 | [8 empty] | 1 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.21 | 10.33 | 2 | http://www.apc.com/shop/us/en/products/P-RBC43 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | Other,Modbus RTU | USB Pwr Sum SmartConnect | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMT3000RM2UC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-01 | 2017-11-14 | United States, Canada | ES_22220_SMT3000RM2UC_11192017072543_6343685
2307490 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface | BN1100M2 | Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BN1100M2W,; Std Exch Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface,BN1100M2Q, | Ac-output UPS | Static | BN1100M2 | 600 | 1100 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.07 |  | 97.8 |  | 98.8 |  | 99 |  | 99.1 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.3 | 13.8 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC160 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN1100M2 | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States | ES_22220_BN1100M2_12072017062654_8014872
2307496 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada | BN1100M2-CA | Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada Factory Serviced,BN1100M2-CAW,; Std Exch Back UPS PRO BN 1100VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada,BN1100M2-CAQ, | Ac-output UPS | Static | BN1100M2 | 600 | 1100 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.07 |  | 97.8 |  | 98.8 |  | 99 |  | 99.1 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.3 | 13.8 | 3 | http://www.apc.com/shop/ca/en/products/P-APCRBC160 | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/ca/en/products/P-BN1100M2-CA | http://www.apc.com/ca/en/who-we-are/sustainability/ | 2018-03-01 | 2017-11-23 | Canada | ES_22220_BN1100M2-CA_12072017065217_9537325
2307502 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1400VA 10 Outlets 2 USB Charging Ports AVR LCD interface | BN1400M2 | Back UPS PRO BN 1400VA 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BN1400M2W,; Std Exch Back UPS PRO BN 1400VA 10 Outlets 2 USB Charging Ports AVR LCD interface,BN1400M2Q, | Ac-output UPS | Static | BN1400M2 | 810 | 1400 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.17 |  | 98.3 |  | 98.9 |  | 99 |  | 98.9 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.6 | 10.4 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC162 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN1400M2 | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-04-01 | 2017-11-23 | United States | ES_22220_BN1400M2_12072017065929_9969673
2307503 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1375VA 10 Outlets 2 USB Charging Ports AVR LCD interface | BN1375M2 | Back UPS PRO BN 1375VA 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BN1375M2W,; Std Exch Back UPS PRO BN 1375VA 10 Outlets 2 USB Charging Ports AVR LCD interface,BN1375M2Q, | Ac-output UPS | Static | BN1400M2 | 810 | 1375 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.17 |  | 98.3 |  | 98.9 |  | 99 |  | 98.9 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.6 | 10.4 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC162 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN1375M2 | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-03-01 | 2017-11-23 | United States | ES_22220_BN1375M2_12072017070702_0422518
2307504 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1350VA 10 Outlets 2 USB Charging Ports AVR LCD interface | BN1350M2 | Back UPS PRO BN 1350VA 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BN1350M2W,; Std Exch Back UPS PRO BN 1350VA 10 Outlets 2 USB Charging Ports AVR LCD interface,BN1350M2Q, | Ac-output UPS | Static | BN1400M2 | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.17 |  | 98.3 |  | 98.9 |  | 99 |  | 98.9 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.6 | 10.4 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC162 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN1350M2 | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States | ES_22220_BN1350M2_12072017072248_1368963
2307505 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface | BN1500M2 | Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BN1500M2W,; Std Exch Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface,BN1500M2Q, | Ac-output UPS | Static | BN1500M2 | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.06 |  | 98.5 |  | 99 |  | 99.1 |  | 99.1 |  | 99 | [8 empty] | 1 | [22 empty] | 99 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.1 | 11.4 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC161 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BN1500M2 | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States | ES_22220_BN1500M2_12072017073844_2324160
2307506 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada | BN1500M2-CA | Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada Factory Serviced,BN1500M2-CAW,; Std Exch Back UPS PRO BN 1500VA 10 Outlets 2 USB Charging Ports AVR LCD interface Canada,BN1500M2-CAQ, | Ac-output UPS | Static | BN1500M2 | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 3.06 |  | 98.5 |  | 99 |  | 99.1 |  | 99.1 |  | 99 | [8 empty] | 1 | [22 empty] | 99 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.1 | 11.4 | 3 | http://www.apc.com/shop/ca/en/products/P-APCRBC161 | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/ca/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/ca/en/products/P-BN1500M2-CA | http://www.apc.com/ca/en/who-we-are/sustainability/ | 2018-03-01 | 2017-11-23 | Canada | ES_22220_BN1500M2-CA_12072017074638_2798172
2307507 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BR 1000VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface | BR1000MS | Back UPS PRO BR 1000VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BR1000MSW,; Std Exch Back UPS PRO BR 1000VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface,BR1000MSQ, | Ac-output UPS | Static | BR1000MS | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 2.97 |  | 97.9 |  | 98.8 |  | 99 |  | 99.1 |  | 99 | [8 empty] | 1 | [22 empty] | 99 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 12.2 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC160 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BR1000MS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States, Canada | ES_22220_BR1000MS_12072017075448_3288458
2307508 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BR 1350VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface | BR1350MS | Back UPS PRO BR 1350VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BR1350MSW,; Std Exch Back UPS PRO BR 1350VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface,BR1350MSQ, | Ac-output UPS | Static | BR1350MS | 810 | 1350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.04 |  | 98.3 |  | 99 |  | 99.1 |  | 99.1 |  | 99.1 | [8 empty] | 1 | [22 empty] | 99.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.3 | 11.4 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC161 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BR1350MS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States, Canada | ES_22220_BR1350MS_12072017080425_3865884
2307509 | Schneider Electric | APC by Schneider Electric | Back UPS PRO BR 1500VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface | BR1500MS | Back UPS PRO BR 1500VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface Factory Serviced,BR1500MSW,; Std Exch Back UPS PRO BR 1500VA SineWave 10 Outlets 2 USB Charging Ports AVR LCD interface,BR1500MSQ, | Ac-output UPS | Static | BR1500MS | 900 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 260 | 100 | 368 | 10 | 6 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 3.1 |  | 98.5 |  | 99 |  | 99.1 |  | 99.1 |  | 99.1 | [8 empty] | 1 | [22 empty] | 99.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.1 | 14.5 | 3 | http://www.apc.com/shop/us/en/products/P-APCRBC163 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | USB Port | Other | USB Power Summary | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-BR1500MS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2017-12-03 | 2017-11-23 | United States, Canada | ES_22220_BR1500MS_12072017081210_4330168
2319705 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V | SMX1500RM2U | APC Smart-UPS X 1500VA Rack/Tower LCD 120V Factory Serviced,SMX1500RM2UW,; Std Exch APC Smart-UPS X 1500VA Rack/Tower LCD 120V,SMX1500RM2UQ, | Ac-output UPS | Static | SMX1500RM2U | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 9.83 |  | 96.5 |  | 97.9 |  | 98.2 |  | 98.2 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC115 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMX1500RM2U | http://www.apc.com/us/en/who-we-are/sustainability/ | 2009-10-02 | 2018-05-10 | United States, Canada | ES_22220_SMX1500RM2U_05142018133637_4997210
2319706 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card | SMX1500RM2UNC | APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card Factory Serviced,SMX1500RM2UNCW,; Std Exch APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card,SMX1500RM2UNCQ, | Ac-output UPS | Static | SMX1500RM2UNC | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.42 |  | 96 |  | 97.6 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 1 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC115 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Modbus TCP | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMX1500RM2UNC | http://www.apc.com/us/en/who-we-are/sustainability/ | 2009-10-07 | 2018-05-10 | United States, Canada | ES_22220_SMX1500RM2UNC_05142018134700_5620975
2320248 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Short Depth Tower/ | SMX2000LVUS | ,SMX2000LVUSQ,; ,SMX2000LVUSW, | Ac-output UPS | Static | SMX2000LV | 1920 | 1800 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | No |  | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 96.1 |  | 97.7 |  | 97.8 |  | 97.9 |  | 97.8 | [8 empty] | 0.99 | [22 empty] | 97.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 11 | 27.6 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC143 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX2000LVUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX2000LVUS_05222018153137_3097965
2320262 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2000VA Rack/Tower LCD 100-127V | SMX2KRMLVNCUS | ,SMX2KRMLVNCUSQ,; ,SMX2KRMLVNCUSW, | Ac-output UPS | Static | SMX2000RMLV2UNC | 1920 | 1800 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 95.9 |  | 97.5 |  | 97.7 |  | 97.8 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 11 | 27.6 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC117 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX2KRMLVNCUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX2KRMLVNCUS_05222018171636_9396930
2320263 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 2200VA Rack/Tower LCD 100-127V TAA | SMX2200RMLVUS | ,SMX2200RMLVUSQ,; ,SMX2200RMLVUSW, | Ac-output UPS | Static | SMX2200RMLV2U | 1980 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 2 | 85 | 432 | 667 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 96.5 |  | 97.9 |  | 98 |  | 98.1 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 9.8 | 25.3 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC117 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX2200RMLV2US | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX2200RMLVUS_05222018185252_5172234
2320291 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Short Depth Tower/ | SMX3000HVTUS | ,SMX3000HVTUSQ,; ,SMX3000HVTUSW, | Ac-output UPS | Static | SMX3000HVT | 2700 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 200-240 | 50-60 | 200-240 | 50-60 | No |  | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 208 | 60 | 208 | 60 |  |  | 97.9 |  | 97.7 |  | 98 |  | 98.2 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.3 | 18 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC143 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX3000HVTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX3000HVTUS_05222018193320_7600647
2320306 | Schneider Electric | APC by Schneider Electric | Rack Convertible LCD 100-127V with Network Card TAA | SMX3000LVNCUS | ,SMX3000LVNCUSQ,; ,SMX3000LVNCUSW, | Ac-output UPS | Static | SMX3000LVNC | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | No |  | 432 | 178 | 483 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 97.1 |  | 98.1 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.3 | 18 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC143 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX3000LVNCUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX3000LVNCUS_05222018195710_9030897
2320308 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/Tower LCD 100-127V TAA | SMX3000RMLVUS | ,SMX3000RMLVUSQ,; ,SMX3000RMLVUSW, | Ac-output UPS | Static | SMX3000RMLV2U | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 97.2 |  | 98.2 |  | 98.1 |  | 98.1 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.3 | 18 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC117 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX3000RMLV2US | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX3000RMLVUS_05222018225315_9595231
2320310 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 3000VA Rack/ | SMX3KRMLVNCUS | ,SMX3KRMLVNCUSQ,; ,SMX3KRMLVNCUSW, | Ac-output UPS | Static | SMX3000RMLV2UNC | 2700 | 2880 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 2 | 85 | 432 | 667 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 97 |  | 98.1 |  | 98.1 |  | 98 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6.3 | 18 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC117 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SMX3KRMLVNCUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SMX3KRMLVNCUS_05222018230629_0389388
2320373 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 2200VA 120V TAA | SRT2200RMXLAUS | ,SRT2200RMXLAUSQ,; ,SRT2200RMXLAUSW, | Ac-output UPS | Static | SRT2200RMXLA | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 2 | 85 | 432 | 584 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 |  |  | 87.7 | 92.6 | 91.2 | 95.8 | 91.7 | 96.8 | 91.9 | 97.2 | 91.6 | 96.6 | [7 empty] | 0.99 | 0.99 | [21 empty] | 91.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.7 | 13.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC141 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT2200RMXLAUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT2200RMXLAUS_05232018164226_3746526
2320379 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 3000VA 120V TAA | SRT3000XLAUS | ,SRT3000XLAUSQ,; ,SRT3000XLAUSW, | Ac-output UPS | Static | SRT3000RMXLA | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 100-127 | 50-60 | 100-127 | 50-60 | No |  | 85 | 432 | 635 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 |  | 37.54 | 89.4 | 94.4 | 91.9 | 96.8 | 91.9 | 97.4 | 91.7 | 97.5 | 91.8 | 97.2 | [7 empty] | 0.99 | 1 | [21 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.8 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC152 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port | Other,Modbus RTU | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT3000RMXLAUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT3000XLAUS_05232018171246_5566102
2320385 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA RM 208V TAA | SRT5KRMXLTUS | ,SRT5KRMXLTUSQ,; ,SRT5KRMXLTUSW, | Ac-output UPS | Static | SRT5KRMXLT | 4250 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 3 | 130 | 432 | 719 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 |  |  | 91.2 | 95.5 | 93.3 | 97.5 | 93.4 | 98 | 93.3 | 98.2 | 93.3 | 97.9 | [7 empty] | 1 | 1 | [21 empty] | 93.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT5KRMXLTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT5KRMXLTUS_05232018173128_6688606
2320387 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 5000VA 208V TAA | SRT5KXLTUS | ,SRT5KXLTUSQ,; ,SRT5KXLTUSW, | Ac-output UPS | Static | SRT5KRMXLT | 4250 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 130 | 719 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 |  |  | 91.2 | 95.5 | 93.3 | 97.5 | 93.4 | 98 | 93.3 | 98.2 | 93.3 | 97.9 | [7 empty] | 1 | 1 | [21 empty] | 93.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4.4 | 12.6 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT5KXLTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT5KXLTUS_05232018174659_7619668
2320393 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 6000VA 208V TAA | SRT6KXLTUS | ,SRT6KXLTUSQ,; ,SRT6KXLTUSW, | Ac-output UPS | Static | SRT6KXLT | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 174 | 719 | 5 | 5 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 |  |  | 92.7 | 96.5 | 94.1 | 98.2 | 94 | 98.7 | 93.7 | 98.9 | 93.9 | 98.6 | [7 empty] | 1 | 1 | [21 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2.3 | 8.3 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT6KXLTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT6KXLTUS_05232018192254_3374068
2320394 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 8000VA 208V TAA | SRT8KXLTUS | ,SRT8KXLTUSQ,; ,SRT8KXLTUSW, | Ac-output UPS | Static | SRT8KRMXLT | 8000 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 432 | 263 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 92.92 |  | 92.8 | 96.3 | 94.3 | 98.1 | 94.4 | 98.6 | 94.1 | 98.8 | 94.3 | 98.5 | [7 empty] | 1 | 1 | [21 empty] | 94.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.2 | 14.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT8KXLTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT8KXLTUS_05232018193624_4184208
2320395 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS SRT 10000VA 208V TAA | SRT10KXLTUS | ,SRT10KXLTUSQ,; ,SRT10KXLTUSW, | Ac-output UPS | Static | SRT10KRMXLT | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial | 208-240 | 50-60 | 208-240 | 50-60 | No |  | 263 | 432 | 715 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 |  | 72 | 93.5 | 97 | 94.5 | 98.4 | 94.3 | 98.8 | 93.8 | 99 | 94.2 | 98.7 | [7 empty] | 1 | 1 | [21 empty] | 94.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3.7 | 11.4 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC140 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Micro-Link | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/shop/us/en/products/P-SRT10KXLTUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-21 | United States, Canada | ES_22220_SRT10KXLTUS_05232018195428_5268236
2320495 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V TAA | SMX1500RMUS | APC Smart-UPS X 1500VA Rack/Tower LCD 120V TAA Factory Serviced,SMX1500RMUSW,; Std Exch APC Smart-UPS X 1500VA Rack/Tower LCD 120V TAA,SMX1500RMUSQ, | Ac-output UPS | Static | SMX1500RM2U | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 |  |  | 96.5 |  | 97.9 |  | 98.2 |  | 98.2 |  | 98.1 | [8 empty] | 1 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC115 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMX1500RMUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-10 | United States, Canada | ES_22220_SMX1500RMUS_05272018034700_2820519
2320496 | Schneider Electric | APC by Schneider Electric | APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card TAA | SMX1500RMNCUS | APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card TAA Factory Serviced,SMX1500RMNCUSW,; Std Exch APC Smart-UPS X 1500VA Rack/Tower LCD 120V with Network Card TAA,SMX1500RMNCUSQ, | Ac-output UPS | Static | SMX1500RM2UNC | 1200 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 490 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 11.42 |  | 96 |  | 97.6 |  | 98 |  | 98.1 |  | 97.9 | [8 empty] | 1 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5.8 | 17.2 | 2 | http://www.apc.com/shop/us/en/products/P-APCRBC115 | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | Serial Port,USB Port,Ethernet | HTTPS,Other,HTTP,SNMP (v1, 2 or 3) | USB Power Sum, Modbus TCP | Yes | http://www.apc.com/us/en/who-we-are/sustainability/recycling-options.jsp | http://www.apc.com/shop/us/en/products/P-SMX1500RMNCUS | http://www.apc.com/us/en/who-we-are/sustainability/ | 2018-05-22 | 2018-05-10 | United States, Canada | ES_22220_SMX1500RMNCUS_05272018034846_2926620
2185264 | Schneider Electric | Schneider Electric | APC Smart-UPS 1500VA LCD RM 2U 120V | SMT1500RMUS |  | Ac-output UPS | Static | SMT1500RM2U | 1000 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial | 120-120 | 50-60 | 120-120 | 50-60 | Yes | 2 | 89 | 432 | 457 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 8.88 |  | 96.3 |  | 97.5 |  | 97.6 |  | 97.4 |  | 97.5 | [8 empty] | 0.99 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 7.2 | 25.8 | 2 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=APCRBC138 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | Serial Port,USB Port | Other | USB Power Sum, Micro-Link | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/eco-friendly-options-for-your-aging-products/eco-friendly-options/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SMT1500RM2U | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2011-03-02 | 2013-07-09 | United States, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SMT1500RMUS_07102013174243_8163284
2194881 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY100K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250D_11182013174553_6753090
2194883 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY100K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DL-PD_11182013174804_6884306
2194885 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY100K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY100K250DR-PD_11182013174920_6960509
2195144 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250-X676 |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250-X676_11202013162714_4834845
2195146 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D_11202013162019_4419570
2195148 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250D-NB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250D-NB_11202013162350_4630637
2195150 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PD_11202013162130_4490003
2195152 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250DL-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DL-PDNB_11202013162244_4564384
2195154 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PD_11202013162505_4705914
2195156 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY125K250DR-PDNB |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K250DR-PDNB_11202013162613_4773883
2195165 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500-X676 |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500-X676_11202013171306_7586126
2195167 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D_11202013170301_6981703
2195169 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500D-NB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500D-NB_11202013170850_7330027
2195171 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500DL-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PDNB_11202013170413_7053375
2195174 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PD_11202013171010_7410075
2195176 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500DR-PDNB |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DR-PDNB_11202013171113_7473051
2195178 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY125K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY125K500DL-PD_11202013173935_9175760
2195183 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY150K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250D_11202013184845_3325574
2195185 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY150K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DL-PD_11202013185000_3400734
2195187 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY150K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY150K250DR-PD_11202013185139_3499617
2195189 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY200K250D |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250D_11202013192309_5389110
2195191 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY200K250DL-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DL-PD_11202013192401_5441445
2195193 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY200K250DR-PD |  | Ac-output UPS | Static | SY100K250DR-PD | 100000 | 100000 | SY250K250DR-PD | 250000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 3100 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 440 | 95 | 98.1 | 96.1 | 98.9 | 96.3 | 99.1 | 96.2 | 99.2 | 95.9 | 98.8 | [7 empty] | 1 | 0.98 | 1850 | 890 | 95.3 | 98.2 | 96.3 | 98.9 | 96.4 | 99.2 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY100K250DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY200K250DR-PD_11202013192500_5500468
2195196 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY250K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500D_11202013194728_6848477
2195198 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY250K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DL-PD_11202013194245_6565591
2195200 | Schneider Electric | Schneider Electric | Symmetra PX250 | SY250K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY250K500DR-PD_11202013194332_6612293
2195202 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY300K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500D_11202013200908_8148214
2195204 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY300K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DL-PD_11202013201001_8201354
2195207 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY300K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY300K500DR-PD_11202013201048_8248616
2195208 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY400K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500D_11202013202942_9382172
2195210 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY400K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DL-PD_11202013203034_9434165
2195212 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY400K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY400K500DR-PD_11202013203423_9663355
2195214 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY500K500D |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500D_11202013204703_0423392
2195216 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY500K500DL-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DL-PD_11202013204748_0468141
2195218 | Schneider Electric | Schneider Electric | Symmetra PX500 | SY500K500DR-PD |  | Ac-output UPS | Static | SY100K500DR-PD | 100000 | 100000 | SY500K500DR-PD | 500000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 380-480 | 50-60 | 380-480 | 50-60 | No |  | 1991 | 5200 | 1070 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 830 | 450 | 95 | 98 | 96.1 | 98.9 | 96.3 | 99.1 | 96.1 | 99.2 | 95.9 | 98.7 | [7 empty] | 1 | 0.98 | 3590 | 1820 | 95.4 | 98.3 | 96.3 | 99 | 96.4 | 99.1 | 96.2 | 99.2 | 96.1 | 98.9 | [7 empty] | 1 | 1 | 96.6 | SYPM25KD | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | NA | NA | NA | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYBFXR8%2D8 | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | None | None |  | Yes | http://www.apc.com/site/recycle/index.cfm/apcs-recycling-and-take-back-programs/ | http://www.apc.com/resource/include/techspec_index.cfm?base_sku=SY500K500DR-PD | http://www.apc.com/site/recycle/index.cfm/energy-efficiency/energy-star/ | 2008-10-11 | 2012-12-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Canada | ES_1105798_AMERICAN POWER CONVERSION CORP (14562) ¦ SY500K500DR-PD_11202013204840_0520687
2256239 | Schneider Electric | Schneider Electric | Galaxy VM 180 kVA UPS Parallel 480-480 V, 65kAIC, Start up 5x8 | GVMPB180KG65S |  | Ac-output UPS | Static | GVMPB180KGS | 162000 | 180000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1057 | 515 | 95.6 | 98.2 | 96.4 | 99 | 96.6 | 99.2 | 96.4 | 99.5 | 96.2 | 98.9 | [7 empty] | 1 | 1 | [21 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP,SNMP (v1, 2 or 3) | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMPB180KG65S_11232015174931_0971477
2256691 | Schneider Electric | Schneider Electric | Galaxy VM 180 kVA Additional UPS for 1+1 480-480 V, 65kAIC, Start up 5x8 | GVMRB180KG65S |  | Ac-output UPS | Static | GVMPB180KGS | 162000 | 180000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1057 | 515 | 95.6 | 98.2 | 96.4 | 99 | 96.6 | 99.2 | 96.4 | 99.5 | 96.2 | 98.9 | [7 empty] | 1 | 1 | [21 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP,SNMP (v1, 2 or 3) | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMRB180KG65S_11232015195432_8472282
2256693 | Schneider Electric | Schneider Electric | Galaxy VM 180 kVA UPS Single 480-480 V, 65kAIC, Start up 5x8 | GVMSB180KG65S |  | Ac-output UPS | Static | GVMPB180KGS | 162000 | 180000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1057 | 515 | 95.6 | 98.2 | 96.4 | 99 | 96.6 | 99.2 | 96.4 | 99.5 | 96.2 | 98.9 | [7 empty] | 1 | 1 | [21 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP,SNMP (v1, 2 or 3) | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB180KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMSB180KG65S_11232015204625_1585904
2260095 | Schneider Electric | Schneider Electric | Galaxy VM 225 kVA UPS Parallel 480-480 V, 65kAIC, Start up 5x8 | GVMPB225KG65S |  | Ac-output UPS | Static | GVMPB225KGS | 202500 | 225000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1038 | 530 | 95.8 | 98.5 | 96.4 | 99.1 | 96.6 | 99.4 | 96.4 | 99.5 | 96.3 | 99 | [7 empty] | 1 | 1 | [21 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMPB225KG65S_02022016002229_2549627
2260097 | Schneider Electric | Schneider Electric | Galaxy VM 225 kVA Additional UPS for 1+1 480-480 V, 65kAIC, Start up 5x8 | GVMRB225KG65S |  | Ac-output UPS | Static | GVMPB225KGS | 202500 | 225000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1038 | 530 | 95.8 | 98.5 | 96.4 | 99.1 | 96.6 | 99.4 | 96.4 | 99.5 | 96.3 | 99 | [7 empty] | 1 | 1 | [21 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMRB225KG65S_02022016002915_2955946
2260099 | Schneider Electric | Schneider Electric | Galaxy VM 225 kVA UPS Single 480-480 V, 65kAIC, Start up 5x8 | GVMSB225KG65S |  | Ac-output UPS | Static | GVMPB225KGS | 202500 | 225000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1038 | 530 | 95.8 | 98.5 | 96.4 | 99.1 | 96.6 | 99.4 | 96.4 | 99.5 | 96.3 | 99 | [7 empty] | 1 | 1 | [21 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB225KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMSB225KG65S_02022016003241_3161351
2260101 | Schneider Electric | Schneider Electric | Galaxy VM 160 kVA UPS Parallel 480-480 V, 65kAIC, Start up 5x8 | GVMPB160KG65S |  | Ac-output UPS | Static | GVMPB160KGS | 144000 | 160000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1072 | 523 | 95.1 | 98.1 | 96.4 | 99 | 96.5 | 99.2 | 96.4 | 99.3 | 96.1 | 99 | [7 empty] | 1 | 1 | [21 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMPB160KG65S_02022016003553_3353796
2260103 | Schneider Electric | Schneider Electric | Galaxy VM 160 kVA Additional UPS for 1+1 480-480 V, 65kAIC, Start up 5x8 | GVMRB160KG65S |  | Ac-output UPS | Static | GVMPB160KGS | 144000 | 160000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1072 | 523 | 95.1 | 98.1 | 96.4 | 99 | 96.5 | 99.2 | 96.4 | 99.3 | 96.1 | 99 | [7 empty] | 1 | 1 | [21 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMRB160KG65S_02022016004919_4159597
2260105 | Schneider Electric | Schneider Electric | Galaxy VM 160 kVA UPS Single 480-480 V, 65kAIC, Start up 5x8 | GVMSB160KG65S |  | Ac-output UPS | Static | GVMPB160KGS | 144000 | 160000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 480-480 | 50-60 | 480-480 | 50-60 | No |  | 1970 | 1002 | 854 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1072 | 523 | 95.1 | 98.1 | 96.4 | 99 | 96.5 | 99.2 | 96.4 | 99.3 | 96.1 | 99 | [7 empty] | 1 | 1 | [21 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 10 | 1 | http://www.apc.com/template/size/apc/sizing_display_options.cfm?option_type=Battery&interface=UPS&famid=483&ups_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | Modbus TCP,HTTPS,HTTP | Modbus RTU | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=GVMSB160KG65S | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2015-09-03 | 2015-11-12 | United States, Canada | ES_22220_GVMSB160KG65S_02022016012811_6491750
2260117 | Schneider Electric | Schneider Electric | Symmetra PX 10kW Scalable to 100kW 208V with Startup | SY10K100F | Symmetra PX 10kW Scalable to 100kW 208V with Startup No Battery,SY10K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY10K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY10K100F_01282016202213_2533850
2260118 | Schneider Electric | Schneider Electric | Symmetra PX 20kW Scalable to 100kW 208V with Startup | SY20K100F | Symmetra PX 20kW Scalable to 100kW 208V with Startup No Battery,SY10K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY20K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY20K100F_01282016202418_2658050
2260119 | Schneider Electric | Schneider Electric | Symmetra PX 30kW Scalable to 100kW 208V with Startup | SY30K100F | Symmetra PX 30kW Scalable to 100kW 208V with Startup No Battery,SY30K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY30K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY30K100F_01282016202811_2891713
2260120 | Schneider Electric | Schneider Electric | Symmetra PX 40kW Scalable to 100kW 208V with Startup | SY40K100F | Symmetra PX 40kW Scalable to 100kW 208V with Startup No Battery,SY40K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY40K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY40K100F_01282016203129_3089029
2260121 | Schneider Electric | Schneider Electric | Symmetra PX 50kW Scalable to 100kW 208V with Startup | SY50K100F | Symmetra PX 50kW Scalable to 100kW 208V with Startup No Battery,SY50K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY50K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY50K100F_01282016203257_3177796
2260122 | Schneider Electric | Schneider Electric | Symmetra PX 60kW Scalable to 100kW 208V with Startup | SY60K100F | Symmetra PX 60kW Scalable to 100kW 208V with Startup No Battery,SY60K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY60K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY60K100F_01282016203617_3377493
2260123 | Schneider Electric | Schneider Electric | Symmetra PX 70kW Scalable to 100kW 208V with Startup | SY70K100F | Symmetra PX 70kW Scalable to 100kW 208V with Startup No Battery,SY70K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY70K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY70K100F_01282016203751_3471899
2260124 | Schneider Electric | Schneider Electric | Symmetra PX 80kW Scalable to 100kW 208V with Startup | SY80K100F | Symmetra PX 80kW Scalable to 100kW 208V with Startup No Battery,SY80K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY80K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY80K100F_01282016203930_3570723
2260125 | Schneider Electric | Schneider Electric | Symmetra PX 90kW Scalable to 100kW 208V with Startup | SY90K100F | Symmetra PX 90kW Scalable to 100kW 208V with Startup No Battery,SY90K100F-NB, | Ac-output UPS | Static | SY10K100F | 10000 | 10000 | SY100K100F | 100000 |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-208 | 50-60 | 208-208 | 50-60 | No |  | 2011 | 1200 | 1070 |  |  |  | Voltage and Frequency Independent | Yes | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 193.82 |  | 91.2 |  | 93.7 |  | 94.2 |  | 94.1 |  | 93.2 | [8 empty] | 1 |  | 1260.6 |  | 93.3 |  | 94.8 |  | 94.9 |  | 94.7 |  | 94.4 | [8 empty] | 1 | 1 | 93.2 | SYPM10KF2 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5.4 | 15.7 | 1 | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SYCFXR9-9 | http://www.apc.com/company/us/en/sustainability/recycling-options/ | Serial Port,Ethernet | HTTPS,HTTP,SNMP (v1, 2 or 3) |  | Yes | http://www.apc.com/company/us/en/sustainability/recycling-options/ | http://www.apc.com/products/resource/include/techspec_index.cfm?base_sku=SY90K100F | http://www.apc.com/company/us/en/sustainability/energy-efficiency/ | 2013-08-15 | 2013-07-15 | United States, Canada | ES_22220_SY90K100F_01282016204138_3698549
2305438 | Socomec, Inc | SOCOMEC Innovative power solutions | NPL-0750-NA | NPL-0750-NA |  | Ac-output UPS | Static | NPL-0750-NA | 450 | 750 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 95 | 158 | 305 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.9 |  | 97.3 |  | 98.2 |  | 98.3 |  | 98.3 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 8 | 3 | https://www.socomec.com/desktop-tower-UPS_en.html |  | USB Port | None |  | No |  | https://www.socomec.com/desktop-tower-UPS_en.html | N/A | 2017-12-01 | 2017-10-23 | United States, Canada | ES_1139531_NPL-0750-NA_10222017231343_5425406
2305439 | Socomec, Inc | SOCOMEC Innovative power solutions | NPL-0350-NA | NPL-0350-NA |  | Ac-output UPS | Static | NPL-0350-NA | 210 | 350 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 95 | 158 | 305 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.62 |  | 95 |  | 97.1 |  | 97.8 |  | 98 |  | 97.1 | [8 empty] | 0.99 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 8 | 3 | https://www.socomec.com/desktop-tower-UPS_en.html |  | None | None |  | No |  | https://www.socomec.com/desktop-tower-UPS_en.html | N/A | 2017-12-01 | 2017-10-23 | United States, Canada | ES_10222017224256_6653610
2101176 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC5758 | ECO750UPS |  | Ac-output UPS | Static | N/A | 450 | 452 | N/A |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 60-60 | 115-120 | 60-60 | No |  | 76 | 178 | 305 | 12 | 6 | 6 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.2 |  | 96.5 |  | 97.9 |  | 98.3 |  | 98.3 |  | 97.6 | [8 empty] | 1 | 1 | [21 empty] | 97.6 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 2.75 | 12.6 | N/A | N/A |  | Ethernet | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4147 | N/A | 2011-11-01 | 2012-10-30 | United States | ES_1097458_ECO750UPS_10272012162222_2587549
2182608 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7951 | SU1500RTXLCD2U |  | Ac-output UPS | Static | AGPS7951 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 100-127 | 60-60 | 100-127 | 60-60 | Yes | 2 | 89 | 445 | 470 |  |  |  | Voltage and Frequency Dependent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 127 | 60 | 0.29 | 0.26 | 88.9 | 92.5 | 91.8 | 95.5 | 92.4 | 96.6 | 92.3 | 97.1 | 92.2 | 92.2 | [7 empty] | 1 | 0.01 | [21 empty] | 95.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 MIN | 12 MIN | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port | Other | RS232 | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=5037 | N/A | 2012-07-01 | 2013-09-17 | United States, Canada | ES_1097458_AGPS7951_06062013124049_7506756
2182609 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7953 | SU3000RTXLCD3U |  | Ac-output UPS | Static | AGPS7953 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 100-127 | 40-70 | 100-127 | 60-60 | Yes | 3 | 133 | 451 | 660 | 9 | 9 | 0 | Voltage and Frequency Dependent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 127 | 60 | 0.31 | 0.3 | 91.3 | 96 | 92.8 | 97.2 | 92.8 | 98 | 92.4 | 97.9 | 92.7 | 92.7 | [7 empty] | 0.01 | 0.01 | [21 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 min 30 sec | 13 min 1 sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port | Other | RS232 | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=5071 | N/A | 2012-06-12 | 2013-09-17 | United States, Canada | ES_1097458_AGPS7953_06062013125219_8486678
2182626 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7950 | SU1000RTXLCD2U |  | Ac-output UPS | Static | AGPS7950 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 100-127 | 40-70 | 100-127 | 60-60 | Yes | 2 | 89 | 445 | 318 | 6 | 6 | 0 | Voltage and Frequency Dependent | No | Multiple-normal-mode | Voltage and Frequency Independent | 127 | 60 | 127 | 60 | 0.23 | 0.22 | 86.6 | 90.9 | 90.6 | 94 | 91.4 | 96.2 | 91.5 | 96.4 | 91.2 | 91.2 | [7 empty] | 1 | 0.01 | [21 empty] | 94.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 MIN | 11 MIN | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port | Other | RS232 | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4980 | N/A | 2011-10-24 | 2013-09-17 | United States, Canada | ES_1097458_AGPS7950_06062013125907_8216158
2182627 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7952 | AGPS7952 |  | Ac-output UPS | Static | AGPS7952 | 1800 | 2200 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-127 | 60-60 | 120-127 | 60-60 | Yes | 2 | 89 | 445 | 483 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 127 | 60 | 0.32 |  | 9 |  | 9.2 |  | 9.2 |  | 9.2 |  | 91.8 | [8 empty] | 0.01 | [22 empty] | 91.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4min 19sec | 13min 20sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | None | Other | RS232 | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4148 | N/A | 2012-03-29 | 2013-05-29 | United States, Canada | ES_1097458_AGPS7952_06062013131220_9772810
2187497 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC7941 | ECO650LCD | ,ECO650LCDTAA, | Ac-output UPS | Static | AGBC7941 | 325 | 650 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 89 | 273 | 146 | 8 | 8 | 4 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 4.14 |  | 95.2 |  | 97.4 |  | 98.1 |  | 94.4 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 MIN 57 SEC | 9 MIN 37 SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4861 | N/A | 2010-12-22 | 2014-09-09 | United States, Canada | ES_1123316_AGBC7941_08062013133031_8504177
2187498 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC7942 | ECO850LCD | ,ECO850LCDTAA, | Ac-output UPS | Static | AGBC7942 | 425 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes |  | 89 | 305 | 178 | 12 | 6 | 6 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.00427 |  | 9.6 |  | 9.8 |  | 9.8 |  | 9.9 |  | 97.9 | [8 empty] | 0.01 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 MIN 45 SEC | 13 MIN 22 SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4148 | N/A | 2011-01-20 | 2014-09-09 | United States, Canada | ES_1123316_AGBC7942_08072013115949_2838117
2187499 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC6806 | INTERNET900U | ,INTERNET900U, INTERNET900TAA, | Ac-output UPS | Static | AGBC6806 | 480 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 78 | 310 | 176 | 12 | 6 | 6 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 3.3 |  | 9.7 |  | 9.8 |  | 9.9 |  | 9.9 |  | 98.5 | [8 empty] | 0.01 | [22 empty] | 98.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 MIN 12 SEC | 11 MIN 21 SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=3657 | N/A | 2007-08-08 | 2016-02-03 | United States, Canada | ES_1123316_AGBC6806_08072013120003_9709044
2187500 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC6780 | POS500 | ,POS500TAA, | Ac-output UPS | Static | AGBC6780 | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes |  | 166 | 91 | 284 | 6 | 3 | 3 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 3.95 |  | 9.5 |  | 9.7 |  | 9.8 |  | 9.8 |  | 97.5 | [8 empty] | 0.01 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 MIN 56 SEC | 15 MIN 49 SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=3742 | N/A | 2007-11-30 | 2014-09-09 | United States, Canada | ES_1123316_AGBC6780_08072013120025_9827989
2188127 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM7010 | SMART3000RMXL2U | ,SM3000RMXL2UTAA, SMART3000RMXLN, SM3000RMXLNTAA, | Ac-output UPS | Static | AGSM7010 | 2885 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 9 | 9 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.347 |  | 94.8 |  | 97.1 |  | 97.4 |  | 97.7 |  | 97.4 | [8 empty] | 1 | [22 empty] | 97.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2min 56sec | 9min 48sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Other,USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4418 | N/A | 2011-07-26 | 2014-09-09 | United States, Canada | ES_1097458_SMART3000RMXL2U, SM3000RMXL2UTAA, SMART3000RMXLN_08152013103841_8931957
2188128 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8209 | SMART3000RM2U |  | Ac-output UPS | Static | AGSM8209 | 2250 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 87 | 440 | 494 | 9 | 9 | 0 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.37 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.7 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 MIN, 27 SEC | 9 MIN, 31 SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Other,Serial Port,USB Port | None | RS232 | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4148 | N/A | 2012-02-29 | 2016-02-03 | United States, Canada | ES_1097458_SMART3000RM2U, SM3000RMNAFTA, SMART3000RM2UN_08152013103947_1281432
2189098 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC5756 | INTERNET550U | ,INTERNET550U, ECO550UPS, ECO550UPSTAA, INTERNET550SER, INTERNET600TAA,; ,INTERNET600U, | Ac-output UPS | Static | AGBC5756 | 300 | 550 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 104-135 | 58-60 | 104-135 | 58-60 | Yes | 1 | 78 | 146 | 276 | 8 | 8 | 4 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 115 | 60 | 4.02 |  | 95.1 |  | 97.3 |  | 98.1 |  | 98.5 |  | 97.5 | [8 empty] | 1 | [22 empty] | 97.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min, 22sec | 9min, 57sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No | No | http://www.tripplite.com/en/products/model.cfm?txtModelID=3063 | N/A | 2007-05-21 | 2014-09-09 | United States, Canada | ES_1123316_INTERNET550U, INTERNET600U; INTERNET550U, ECO550UPS, ECO550UPSTAA, INTERNET550SER _08282013094826_5214596
2191606 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | SU2200RTXLCD2U | SU2200RTXLCD2U |  | Ac-output UPS | Static | AGPS7952 | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 120-127 | 40-70 | 120-127 | 60-60 | Yes | 2 | 89 | 445 | 483 | 7 | 7 | 0 | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 127 | 60 | 0.32 | 0.33 | 90.1 | 94.4 | 92 | 96.6 | 91.7 | 97.7 | 91.6 | 97 | 91.8 | 91.8 | [7 empty] | 1 | 0 | [21 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 MIN 19 SEC | 13MIN 20SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=5069 | N/A | 2012-03-29 | 2016-08-09 | United States, Canada | ES_1123316_SU2200RTXLCD2U, AGPS7952_09182013152217_9389813
2195049 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGOM6032 | OMNIVS1000 | ,OMNIVS1000 NAFTA, OMNIVS1000TAA, | Ac-output UPS | Static | OMNIVS1000 | 500 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes |  | 381 | 445 | 286 | 8 | 6 | 2 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.92 |  | 91.8 |  | 95.9 |  | 97.1 |  | 97.5 |  | 97 | [8 empty] | 0.01 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min 11sec | 9min 51sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=2656 | N/A | 2005-06-25 | 2014-09-09 | United States, Canada | ES_1097458_AGOM6032_11192013121230_5936673
2195141 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM3000MJR31 | SMART3000VS | ,SMART3000VSTAA, | Ac-output UPS | Static | AGSM3000MJR31 | 2250 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 115-120 | 60-60 | Yes |  | 362 | 235 | 305 | 10 | 10 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.419 |  | 93.1 |  | 96 |  | 97.2 |  | 97.3 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4min | 14min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port | SNMP (v1, 2 or 3) |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=2721 | N/A | 2005-06-26 | 2014-09-09 | United States, Canada | ES_1097458_AGSM3000MJR31_11202013104326_3109342
2195142 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM6819 | SMART3000RMOD2U |  | Ac-output UPS | Static | AGSM6819 | 2880 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 100-127 | 60-60 | 100-127 | 60-60 | Yes |  | 89 | 445 | 610 | 7 | 7 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 127 | 60 | 127 | 60 | 0.286 |  | 94.6 |  | 96.9 |  | 97.9 |  | 97.8 |  | 97.6 | [8 empty] | 0.01 | [22 empty] | 97.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4min | 11min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port | None | EPO | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=4249 | N/A | 2008-12-05 | 2013-09-12 | United States, Canada | ES_1097458_AGSM6819_11202013104858_2552550
2195143 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGBC5053 | AVR750U | ,AVR750UTAA, | Ac-output UPS | Static | AGBC5053 | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 102 | 305 | 178 | 12 | 6 | 6 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.843 |  | 93 |  | 96.2 |  | 97.3 |  | 97.8 |  | 97.1 | [8 empty] | 0.01 | [22 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min | 10min, 26sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=3141 | N/A | 2010-02-02 | 2014-09-09 | United States, Canada | ES_1097458_AGBC5053_11202013105415_7685381
2204942 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM5060 | SMART1000RM1U | ,SMART1000RM1U, SM1000RM1UTAA, SMART1000RM1UN, | Ac-output UPS | Static | AGSM5060 | 800 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 44 | 445 | 425 | 6 | 6 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.979 |  | 9.4 |  | 9.7 |  | 9.8 |  | 9.9 |  | 96.7 | [8 empty] | 0.01 | [22 empty] | 96.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min 55sec | 14min 12sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.tripplite.com/en/products/model.cfm?txtModelID=3054 | N/A | 2012-01-05 | 2015-11-10 | United States, Canada | ES_1123316_SMART1000RM1U_02212014121644_3282788
2245998 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS8296 | SU3000LCD2UHV |  | Ac-output UPS | Static | AGPS8296 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 88 | 438 | 600 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.49 | 0.51 | 89.2 | 92.2 | 91.8 | 96.3 | 92.3 | 96.5 | 92 | 97.2 | 92.1 | 96.6 | [7 empty] | 0.1 | 0.01 | [21 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 13min, 35sec | 5min, 6 sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2015-12-01 | 2015-08-17 | United States, Europe, Canada | ES_1123316_SU3000LCD2UHV_08192015114852_5311217
2245999 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS8296 | SU3000LCD2UHV |  | Ac-output UPS | Static | AGPS8296 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 88 | 438 | 600 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.49 | 0.51 | 89.2 | 92.2 | 91.8 | 96.3 | 92.3 | 96.5 | 92 | 97.2 | 92.1 | 96.6 | [7 empty] | 0.1 | 0.01 | [21 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 13min, 35sec | 5min, 6 sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2015-12-01 | 2015-08-17 | United States, Europe, Canada | ES_1097458_SU3000LCD2UHV_08192015121826_4307634
2246000 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7959 | SUINT3000LCD2U |  | Ac-output UPS | Static | AGPS7959 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 88 | 438 | 600 | 8 | 8 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.53 | 0.51 | 89 | 92.6 | 91.6 | 95.6 | 91.9 | 96.4 | 91.8 | 96.9 | 91.8 | 96.3 | [7 empty] | 0.1 | 0.1 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 13min, 27sec | 5min, 3sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2015-12-01 | 2015-08-17 | United States, Europe, Canada | ES_1097458_SUINT3000LCD2U_08192015121926_9255491
2246027 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0067 | OMNI1500LCDT |  | Ac-output UPS | Static | AG-0067 | 810 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 203 | 146 | 396 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.05 |  | 9.7 |  | 9.8 |  | 9.9 |  | 9.9 |  | 98.6 | [8 empty] | 0.01 | [22 empty] | 98.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 1min, 34sec | 7min, 30sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/line-interactive-ups-system-1500va-120v-lcd-screen-usb-port~OMNI1500LCDT/ | N/A | 2012-11-30 | 2015-08-19 | United States, Canada | ES_1097458_OMNI1500LCDT_08192015210221_1537335
2252600 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7958 | SUINT2200LCD2U |  | Ac-output UPS | Static | AGPS7958 | 1980 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 88 | 438 | 483 | 9 | 9 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.439 | 0.4324 | 89.5 | 92.5 | 92.6 | 95.8 | 93.5 | 97 | 93.8 | 97.5 | 89 | 93.3 | [7 empty] | 0.01 | 0.01 | [21 empty] | 93.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 min | 13min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2015-12-01 | 2015-11-09 | United States, Europe, Canada | ES_1123316_SUINT2200LCD2U_11132015110039_7271923
2256803 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGOM7057 | SMART1000LCDU |  | Ac-output UPS | Static | AGOM7057 | 500 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | No |  | 301 | 93 | 184 | 8 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.098 |  | 92.6 |  | 96 |  | 97.2 |  | 97.7 |  | 97 | [8 empty] | 0.01 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min 8sec | 10min 2 sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | in preparation | N/A | 2016-04-01 | 2016-01-15 | United States, Canada | ES_1123316_SMART1000LCDU_01152016155331_1108731
2259879 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS8295 | SUINT1500LCD2U |  | Ac-output UPS | Static | AGPS8295 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 88 | 438 | 496 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.45 | 0.41 | 8.6 | 9 | 9 | 9.5 | 9.2 | 9.6 | 9.3 | 9.7 | 8.9 | 9.2 | [7 empty] | 0.01 | 0.01 | [21 empty] | 9.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 min 28 sec | 12 min 35 sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2016-03-01 | 2016-02-03 | United States, Europe, Canada | ES_1123316_SUINT1500LCD2U_02102016091148_7823162
2267557 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS8294 | SUINT1000LCD2U |  | Ac-output UPS | Static | AGPS8294 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 200-240 | 40-70 | 200-240 | 50-60 | Yes | 2 | 89 | 445 | 318 | 6 | 6 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.314 | 0.281 | 86.1 | 89.4 | 90.8 | 94.1 | 92.6 | 95.9 | 92.4 | 96.6 | 8.8 | 9.2 | [7 empty] | 0.01 | 0.01 | [21 empty] | 9.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 min | 11 min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | in preparation | N/A | 2016-05-01 | 2016-03-24 | United States, Europe, Canada | ES_1123316_SUINT1000LCD2U_03302016094816_3671704
2274528 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | SU2200RTXLCDN | SU2200RTXLCDN | SU2200RTLCDN530, SU22002U-A73, SU2200RTXLCDBP1,SU2200RTLCDN530, SU22002U-A73, SU2200RTXLCDBP1, | Ac-output UPS | Static | AGPS7952 | 1800 | 2200 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 120-127 | 40-70 | 120-127 | 60-60 | Yes | 2 | 89 | 445 | 483 | 7 | 7 | 0 | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 127 | 60 | 0.32 | 0.33 | 90.1 | 94.4 | 92 | 96.6 | 91.7 | 97.7 | 91.6 | 97 | 91.8 | 91.8 | [7 empty] | 1 | 0 | [21 empty] | 97.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 MIN 19 SEC | 13MIN 20SEC | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port,Ethernet | SNMP (v1, 2 or 3),HTTP |  | No |  | http://www.tripplite.com/main/search/q/su2200rtxlcdn | N/A | 2012-03-29 | 2016-08-09 | United States, Canada | ES_1097458_SU2200RTXLCDN_08102016122153_6927777
2278540 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-013A | SU3000RTXL2UA |  | Ac-output UPS | Static | AG-013A | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 100-120 | 50-60 | Yes | 2 | 88 | 438 | 616 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 0.441 | 0.41 | 8.9 | 9.4 | 9.1 | 9.6 | 9.2 | 9.7 | 9.2 | 9.7 | 8.9 | 9.1 | [7 empty] | 0.01 | 0.01 | [21 empty] | 9.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4min, 30sec | 13min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/ | N/A | 2016-10-29 | 2016-09-07 | United States, Canada | ES_1123316_SU3000RTXL2UA_09082016124106_1411542
2296664 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8208 | SM2200RMXL2UTAA |  | Ac-output UPS | Static | AGSM8208 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 8 | 8 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.3 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.8 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 minutes, 36 seconds | 11 minutes, 42 seconds | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None | EPO | No |  | https://www.tripplite.com/taa-smartpro-120v-2.2kva-1.92kw-line-interactive-sine-wave-ups-2u-extended-run-network-card-options-lcd-usb-db9~SM2200RMXL2UTAA/ | N/A | 2012-04-09 | 2017-05-25 | United States, Canada | ES_1123316_SM2200RMXL2UTAA_05252017212110_1911283
2296665 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8208 | SMART2200RMXL2U |  | Ac-output UPS | Static | AGSM8208 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 8 | 8 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.3 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.8 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 minutes, 36 seconds | 11 minutes, 42 seconds | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None | EPO | No |  | https://www.tripplite.com/smartpro-120v-2.2kva-1.92kw-line-interactive-sine-wave-ups-2u-rack-tower-extended-run-snmpwebcard-option-lcd-display-usb-db9-serial~SMART2200RMXL2U/ | N/A | 2012-03-31 | 2017-05-25 | United States, Canada | ES_1123316_SMART2200RMXL2U_05262017123701_3955701
2296666 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8208 | SMART2200RMXLN |  | Ac-output UPS | Static | AGSM8208 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 8 | 8 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.3 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.8 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 minutes, 36 seconds | 11 minutes, 42 seconds | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | SNMP (v1, 2 or 3) | EPO | No |  | https://www.tripplite.com/smartpro-120v-2.2kva-1.92kw-line-interactive-sine-wave-ups-2u-rack-tower-extended-run-pre-installed-snmpwebcard-lcd-display-usb-db9-serial~SMART2200RMXLN/ | N/A | 2016-11-03 | 2017-05-25 | United States, Canada | ES_1123316_SMART2200RMXL2UN_05262017123710_4861896
2296667 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8208 | SMART2200RM2U |  | Ac-output UPS | Static | AGSM8208 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 8 | 8 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.3 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.8 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 minutes, 36 seconds | 11 minutes, 42 seconds | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None | EPO | No |  | https://www.tripplite.com/smartpro-120v-2.2kva-1.92kw-line-interactive-sine-wave-ups-2u-rack-tower-snmpwebcard-option-lcd-display-usb-db9-serial~SMART2200RM2U/ | N/A | 2012-03-13 | 2017-05-25 | United States, Canada | ES_1123316_SMART2200RM2U_05262017123719_3703368
2296668 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM8208 | SMART2200RM2UN |  | Ac-output UPS | Static | AGSM8208 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 2 | 89 | 445 | 483 | 8 | 8 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.3 |  | 9.4 |  | 9.6 |  | 9.7 |  | 9.8 |  | 96.9 | [8 empty] | 0.01 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 minutes, 36 seconds | 11 minutes, 42 seconds | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | SNMP (v1, 2 or 3) | EPO | No |  | https://www.tripplite.com/main/search?q=SMART2200RM2UN | N/A | 2016-11-03 | 2017-05-25 | United States, Canada | ES_1123316_SMART2200RM2UN_05262017123727_1570158
2300103 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0070 | SMX2200XLRT2U |  | Ac-output UPS | Static | AG-0007 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 89 | 445 | 495 | 8 | 8 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 50 | 230 | 50 | 0.362 |  | 9.3 |  | 9.7 |  | 9.7 |  | 9.8 |  | 9.7 | [8 empty] | 0.01 | [22 empty] | 9.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4min, 59sec | 11min, 52sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | None |  | No |  | https://www.tripplite.com/smartpro-230v-2.2kva-1.92kw-line-interactive-sine-wave-ups-2u-rack-tower-extended-run-snmpwebcard-option-lcd-display-usb-db9-serial~SMX2200XLRT2U/ | N/A | 2013-04-26 | 2017-07-18 | United States, Europe, Canada | ES_1097458_SMX2200XLRT2U_07182017213658_5913739
2303666 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGSM5246 | SMART5000TEL3U |  | Ac-output UPS | Static | AGSM5246 | 3750 | 4500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 208-208 | 60-60 | 208-208 | 60-60 | Yes | 3 | 133 | 445 | 635 | 5 | 5 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 208 | 60 | 208 | 60 | 0.47 |  | 9.5 |  | 9.7 |  | 9.8 |  | 9.9 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8min, 35sec | 19min, 40sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port | Other | SNMP (vG) | No |  | https://www.tripplite.com/smartpro-208v-5kva-3.75kw-line-interactive-sine-wave-ups-3u-rack-tower-snmpwebcard-option-usb-db9-serial~SMART5000TEL3U/ | N/A | 2012-08-21 | 2017-09-15 | United States, Canada | ES_1097458_SMART5000TEL3U_09152017151624_1275724
2312596 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0163 | SMART2200RM2UL |  | Ac-output UPS | Static | AG-0163 | 1920 | 2200 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 87 | 439 | 489 | 8 | 0 | 8 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.204 |  | 9.5 |  | 9.8 |  | 9.8 |  | 9.9 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Lithium-ion Battery | Integral | No | 5min 6sec | 11min 39sec | 5 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port,Ethernet | Other | SNMP vG | No |  | https://www.tripplite.com/smartpro-120v-2.2kva-1.92kw-line-interactive-sine-wave-ups-lithium-iron-phosphate-lifepo4-batteries-2u-lcd-usb-db9~SMART2200RM2UL | N/A | 2016-11-09 | 2018-03-09 | United States, Canada | ES_1097458_SMART2200RM2UL_03122018094741_1606687
2312597 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-8897 | SMART1500RM2UL |  | Ac-output UPS | Static | AG-8897 | 1440 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 87 | 439 | 489 | 8 | 0 | 8 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.205 |  | 9.7 |  | 9.7 |  | 9.9 |  | 9.8 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Lithium-ion Battery | Integral | No | 7min 4sec | 15min 26sec | 5 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port,Ethernet | Other | SNMP vG | No |  | https://www.tripplite.com/ | N/A | 2018-04-01 | 2018-03-09 | United States, Canada | ES_1097458_SMART1500RM2UL_03122018095406_8652159
2312598 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-02B4 | SMART3000RM2UL |  | Ac-output UPS | Static | AG-02B4 | 2250 | 3000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 87 | 440 | 494 | 9 | 9 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.32 |  | 9.5 |  | 9.7 |  | 9.8 |  | 9.8 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Lithium-ion Battery | Integral | No | 3min, 27sec | 9min, 31sec | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port,Ethernet | Other | SNMP (vG) | No |  | http://www.tripplite.com/ | N/A | 2018-04-01 | 2018-03-09 | United States, Canada | ES_1097458_SMART3000RM2UL_03122018101054_1637408
2324023 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-87C2 | ECO1300LCD |  | Ac-output UPS | Static | AG-87C2 | 720 | 1300 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 99 | 410 | 5 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.048 |  | 9.8 |  | 9.8 |  | 9.9 |  | 9.8 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min | 11min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/products/ | N/A | 2018-05-01 | 2018-08-06 | United States, Canada | ES_1097458_ECO1300LCD_08072018090128_6518673
2324024 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-87C3 | ECO1500LCD |  | Ac-output UPS | Static | AG-87C3 | 900 | 1440 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 99 | 410 | 5 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.059 |  | 9.8 |  | 9.9 |  | 9.8 |  | 9.8 |  | 9.9 | [8 empty] | 0.01 | [22 empty] | 9.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3min | 11min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/products/ | N/A | 2018-05-01 | 2018-08-06 | United States, Canada | ES_1097458_ECO1500LCD_08072018090704_1289123
2324049 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-87C1 | ECO1000LCD |  | Ac-output UPS | Static | AG-87C1 | 600 | 1000 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 99 | 288 | 4 | 4 | 4 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.052 |  | 9.6 |  | 9.8 |  | 9.8 |  | 9.8 |  | 9.8 | [8 empty] | 0.01 | [22 empty] | 9.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2min | 7min | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | No |  | http://www.tripplite.com/en/products/ | N/A | 2018-05-01 | 2018-08-07 | United States, Canada | ES_1097458_ECO1000LCD_08082018113702_4529952
2324419 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AGPS7255 | SU5000RT4UHV |  | Ac-output UPS | Static | AGPS7255 | 4500 | 5000 |  |  |  | Multi-Mode Line Interactive | ac - Other | Commercial,Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 4 | 174 | 445 | 525 | 4 | 4 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 240 | 60 | 240 | 60 | 0.4 | 33.45 | 89.4 | 94.3 | 91.5 | 94.6 | 91.6 | 97.3 | 91.3 | 97.8 | 91.8 | 97.7 | [7 empty] | 0.99 | 1 | [21 empty] | 93.3 | N/A | Battery | Other | Integral | No | 4 | 11 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,USB Port,Ethernet | Other | SNMP (vC) | No |  | https://www.tripplite.com/smartonline-208-240v-5kva-4.5kw-double-conversion-ups-4u-rack-tower-extended-run-snmpwebcard-option-usb-db9-serial~SU5000RT4UHV | N/A | 2013-11-12 | 2018-08-14 | United States, Canada | ES_1097458_SU5000RT4UHV_08162018084045_8560149
2324420 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-013A | SU3000RTXL2UA |  | Ac-output UPS | Static | AG-013A | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer | 120-120 | 60-60 | 100-120 | 50-60 | Yes | 2 | 88 | 438 | 616 | 7 | 7 | 0 | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 0.4 | 0.335 | 89.4 | 94.3 | 91.5 | 94.6 | 91.6 | 97.3 | 91.3 | 97.8 | 91.5 | 96.6 | [7 empty] | 0.99 | 1 | [21 empty] | 92.8 | N/A | Battery | Other | Integral | No | 5 | 13 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Serial Port,Other,USB Port,Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/smartonline-120v-3kva-2.7kw-on-line-double-conversion-ups-2u-rack/tower-extended-run-network-card-option-energy-star~SU3000RTXL2U | N/A | 2016-10-29 | 2018-08-14 | United States, Canada | ES_1097458_SU3000RTXL2UA_08162018131746_2059049
2329678 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-87C2 | ECO1300LCD |  | Ac-output UPS | Static | AG-87C2 | 720 | 1300 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No | 3 | 279 | 99 | 410 | 5 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.585 |  | 97.2 |  | 98.5 |  | 98.7 |  | 98.8 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/line-interactive-ups-with-usb-and-10-outlets-1300va-720w-avr-eco-series~ECO1300LCD | N/A | 2018-05-01 | 2018-11-13 | United States, Canada | ES_1097458_ECO1300LCD_11142018104423_2930264
2329679 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-87C3 | ECO1500LCD |  | Ac-output UPS | Static | AG-87C3 | 900 | 1440 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No | 1 | 279 | 99 | 410 | 5 | 5 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 0.06 |  | 97.7 |  | 98.6 |  | 98.8 |  | 98.7 |  | 98.7 | [8 empty] | 1 | [22 empty] | 98.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/line-interactive-ups-with-usb-and-10-outlets-1500va-900w-avr-eco-series~ECO1500LCD | N/A | 2018-05-01 | 2018-11-14 | United States, Canada | ES_1097458_ECO1500LCD_11142018153445_7374371
2329903 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0317 | INTERNET900U | ,INTERNET900TAA, | Ac-output UPS | Static | AG-0317 | 480 | 900 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 60-60 | 120-120 | 60-60 | Yes | 1 | 85 | 130 | 320 | 12 | 6 | 6 | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 0.024 |  | 98.7 |  | 99.5 |  | 99.7 |  | 99.8 |  | 99.5 | [8 empty] | 1 | [22 empty] | 99.5 | N/A | Battery | Other | Integral | No | 2 | 8 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/internet-office-120v-900va-480w-standby-ups-ultra-compact-desktop-usb~INTERNET900U | N/A | 2018-11-23 | 2018-11-14 | United States, Canada | ES_1097458_INTERNET900U_11152018194040_2707105
2330332 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0314 | INTERNET750U |  | Ac-output UPS | Static | AG-0314 | 450 | 750 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 85 | 130 | 320 | 12 | 6 | 6 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.34 |  | 98.6 |  | 99.4 |  | 99.7 |  | 99.7 |  | 99.4 | [8 empty] | 1 | [22 empty] | 99.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 2 | 9 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/internet-office-120v-750va-450w-standby-ups-ultra-compact-desktop-usb~INTERNET750U | N/A | 2018-12-28 | 2018-11-27 | United States, Canada | ES_1097458_INTERNET750U_11282018160442_2182782
2330651 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0310 | ECO550UPS |  | Ac-output UPS | Static | AG-0310 | 300 | 550 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 105 | 110 | 185 | 10 | 5 | 5 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 0.022 |  | 98 |  | 99.2 |  | 99.4 |  | 99.6 |  | 99.1 | [8 empty] | 1 | [22 empty] | 99.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 1 | 5 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | https://www.tripplite.com/eco-series-120v-550va-300w-energy-saving-standby-ups-usb-8-outlets~ECO550UPS | N/A | 2018-12-28 | 2018-12-03 | United States, Canada | ES_1097458_ECO550UPS_12032018160154_6894680
2330761 | Tripp Lite, Div of Trippe MFG., Co. | Tripp Lite | AG-0067 | OMNI1500LCDT |  | Ac-output UPS | Static | AG-0067 | 810 | 1500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Commercial,Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 203 | 146 | 396 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.05 |  | 97.9 |  | 98.7 |  | 98.8 |  | 98.8 |  | 98.8 | [8 empty] | 0.99 | [22 empty] | 98.8 | N/A | Battery | Other | Integral | No | 2 | 8 | 3 | N/A | http://www.tripplite.com/en/support/recycling-program.cfm | USB Port,Ethernet | None |  | Yes | http://www.tripplite.com/en/support/recycling-program.cfm | http://www.tripplite.com/line-interactive-ups-system-1500va-120v-lcd-screen-usb-port~OMNI1500LCDT/ | N/A | 2012-11-30 | 2018-12-04 | United States, Canada | ES_1097458_OMNI1500LCDT_12042018194207_4185590
2031462 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APM | NR Series |  | Ac-output UPS | Static | NRA90CC | 15000 | 15000 | NRF90CC | 90000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 208-208 | 60-60 | 208-208 | 60-60 | No |  | 2000 | 800 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 172.89 | 177.24 | 92.4 | 94.8 | 93.6 | 97.1 | 93.4 | 97.7 | 92.6 | 98.1 | 93.3 | 96.7 | [7 empty] | 1 | 0.99 | 899.5 | 883.08 | 93 | 95.5 | 93.9 | 97.1 | 93.5 | 97.5 | 92.6 | 97.6 | 93.6 | 96.8 | [7 empty] | 0.99 | 0.99 | 93.3 | 2351752 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 69 | 153 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2012-09-27 | 2012-10-10 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (754541) ¦ NR Series_10102012173318_0398517
2169771 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-10000RT208 |  | Ac-output UPS | Static | GXT3-10000RT208 | 9000 | 10000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 6 | 261 | 430 | 672 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 121.57 |  | 91.1 |  | 92.5 |  | 92.4 |  | 91.6 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 | 14 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2010-03-05 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-10000RT208_01222013155822_0302451
2169772 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-1000RT120 | Liebert GVG3,GVG3-1000RT120, | Ac-output UPS | Static | GXT3-1000RT120 | 900 | 1000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 31.71 |  | 84.6 |  | 88.6 |  | 88.9 |  | 88.4 |  | 88.7 | [8 empty] | 0.99 | [22 empty] | 88.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 17 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-20 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-1000RT120_01222013155832_0312275
2169773 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-1500RT120 | Liebert GVG3,GVG3-1500RT120, | Ac-output UPS | Static | GXT3-1500RT120 | 1350 | 1500 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 47.57 |  | 84.9 |  | 89 |  | 90.1 |  | 90 |  | 89.7 | [8 empty] | 0.99 | [22 empty] | 89.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-20 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-1500RT120_01222013155848_0328117
2169774 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-2000RT120 | Liebert GVG3,GVG3-2000RT120, | Ac-output UPS | Static | GXT3-2000RT120 | 1746 | 1940 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 46.32 |  | 86.7 |  | 89.8 |  | 90.1 |  | 89.6 |  | 89.9 | [8 empty] | 0.99 | [22 empty] | 89.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-20 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-2000RT120_01222013155902_0342634
2169775 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-3000RT120 | Liebert GVG3,GVG3-3000RT120, | Ac-output UPS | Static | GXT3-3000RT120 | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 68.83 |  | 87.2 |  | 89.9 |  | 89.9 |  | 89.2 |  | 89.7 | [8 empty] | 0.99 | [22 empty] | 89.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-02 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-3000RT120_01222013155914_0354372
2169776 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-3000RT208 |  | Ac-output UPS | Static | GXT3-3000RT208 | 2700 | 3000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 76.4 |  | 86.7 |  | 90.4 |  | 91.1 |  | 90.9 |  | 90.8 | [8 empty] | 0.99 | [22 empty] | 90.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 3 | 11 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-02 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-3000RT208_01222013155926_0366674
2169777 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-5000RT208 |  | Ac-output UPS | Static | GXT3-5000RT208 | 4000 | 5000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 4 | 173 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 81.65 |  | 89.7 |  | 92.2 |  | 92.6 |  | 92.6 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 6 | 16 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2010-04-09 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-5000RT208_01222013155937_0377813
2169778 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-6000RT208 | Liebert GVG3,GVG3-6000RT208, | Ac-output UPS | Static | GXT3-6000RT208 | 4800 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 4 | 173 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 82.9 |  | 90.2 |  | 92.6 |  | 92.9 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 4 | 13 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2010-04-09 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-6000RT208_01222013155950_0390394
2169779 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-6000RTL630 |  | Ac-output UPS | Static | GXT3-6000RTL630 | 4200 | 6000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes | 5 | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 230 | 60 | 230 | 60 | 68.98 |  | 90.8 |  | 93.5 |  | 93.8 |  | 93.6 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 8 | 19 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2010-03-26 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-6000RTL630_01222013160010_0410258
2169780 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-700RT120 |  | Ac-output UPS | Static | GXT3-700RT120 | 630 | 700 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.6 |  | 83.5 |  | 88.5 |  | 89.6 |  | 89.8 |  | 89.3 | [8 empty] | 0.99 | [22 empty] | 89.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 11 | 27 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2009-09-20 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-700RT120_01222013160023_0423691
2169781 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert GXT3 | GXT3-8000RT208 |  | Ac-output UPS | Static | GXT3-8000RT208 | 7200 | 8000 |  |  |  | Double Conversion | ac - Double Conversion (VFI) | Data Center | 120-240 | 50-60 | 120-240 | 50-60 | Yes | 6 | 261 | 430 | 672 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 117.3 |  | 90.4 |  | 92.4 |  | 97 |  | 92.4 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 7 | 20 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2010-03-05 | 2013-01-17 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT3-8000RT208_01222013155811_0291451
2175526 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APM 45K frame with top fan assembly | NR Series 45k frame with top fan |  | Ac-output UPS | Static | NRA40CC | 15000 | 15000 | NRC40CC | 45000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 208-208 | 60-60 | 208-208 | 60-60 | No |  | 2140 | 800 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 347.16 | 348.24 | 88.5 | 91 | 91.7 | 95.1 | 92.2 | 96.4 | 91.8 | 97 | 91 | 94.4 | [7 empty] | 1 | 1 | 629.39 | 621.66 | 91.6 | 94 | 93.2 | 96.5 | 93.1 | 97.3 | 92.4 | 97.6 | 92.7 | 96.1 | [7 empty] | 1 | 1 | 91 | 2351752 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 69 | 153 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2012-09-27 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ NR Series 45k frame with top fan_03192013141234_2354490
2175527 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APM 90K frame with top fan assembly | NR Series 90k frame with top fan |  | Ac-output UPS | Static | NRB90CC | 30000 | 30000 | NRF90CC | 90000 |  | Multi-Mode Double Conversion | ac - Other | Data Center | 208-208 | 60-60 | 208-208 | 60-60 | No |  | 2178 | 800 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 170.41 | 675.77 | 88.8 | 91.3 | 91.8 | 95.1 | 92.2 | 96.4 | 91.8 | 96.9 | 91.2 | 94.5 | [7 empty] | 1 | 1 | 1256.52 | 1226.38 | 91.6 | 94.1 | 93.1 | 96.4 | 92.9 | 97 | 92.2 | 97.2 | 92.7 | 96 | [7 empty] | 1 | 1 | 91.2 | 2351752 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 69 | 153 | 1 | http://www.enersys.com/ |  | None | None |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/LiebertAPMOn-lineUPS15-90kW.aspx | N/A | 2012-09-27 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ NR Series 90k frame with top fan_03192013141308_2388577
2177849 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40MM11MA, Multi-Module MM |  | Ac-output UPS | Static | 40SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18327.48 | 18287.76 | 92.1 | 93.2 | 94.1 | 96.3 | 94.2 | 97.3 | 93.8 | 97.7 | 93.6 | 95.8 | [7 empty] | 0.92 | 1 | [21 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2011-11-10 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40MM11MA, Multi-Module MM_03272013152122_7682773
2177850 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40MM12MA, Multi-Module MM |  | Ac-output UPS | Static | 40SN12MA | 1125000 | 1125000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18323.24 | 18289.52 | 92.3 | 93.6 | 94.2 | 96.4 | 94.4 | 97.3 | 93.8 | 97.8 | 93.8 | 95.9 | [7 empty] | 0.92 | 1 | [21 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2012-04-16 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40MM12MA, Multi-Module MM_03272013175522_6922836
2177851 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SA11MA, Single Module - SMS |  | Ac-output UPS | Static | 40SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18327.48 | 18287.76 | 92.1 | 93.2 | 94.1 | 96.3 | 94.2 | 97.3 | 93.8 | 97.7 | 93.6 | 95.8 | [7 empty] | 0.92 | 1 | [21 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2011-11-10 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SA11MA, Single Module - SMS_03272013152013_7613609
2177852 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SA12MA, Single Module - SMS |  | Ac-output UPS | Static | 40SN12MA | 1125000 | 1125000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18323.24 | 18289.52 | 92.3 | 93.6 | 94.2 | 96.4 | 94.4 | 97.3 | 93.8 | 97.8 | 93.8 | 95.9 | [7 empty] | 0.92 | 1 | [21 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2012-04-16 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SA12MA, Single Module - SMS_03272013175450_6890938
2177853 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SN11MA, 1+n parallel redundant - SMS |  | Ac-output UPS | Static | 40SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18327.48 | 18287.76 | 92.1 | 93.2 | 94.1 | 96.3 | 94.2 | 97.3 | 93.8 | 97.7 | 93.6 | 95.8 | [7 empty] | 0.92 | 1 | [21 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2011-11-10 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SN11MA, 1+n parallel redundant - SMS_03272013151849_7529280
2177854 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SR12MA, 1+1 Redundant - SMS |  | Ac-output UPS | Static | 40SN12MA | 1125000 | 1125000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18323.24 | 18289.52 | 92.3 | 93.6 | 94.2 | 96.4 | 94.4 | 97.3 | 93.8 | 97.8 | 93.8 | 95.9 | [7 empty] | 0.92 | 1 | [21 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2012-04-16 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SR12MA, 1+1 Redundant - SMS_03272013175129_6689170
2177855 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SN12MA, 1+n parallel redundant - SMS |  | Ac-output UPS | Static | 40SN12MA | 1125000 | 1125000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18323.24 | 18289.52 | 92.3 | 93.6 | 94.2 | 96.4 | 94.4 | 97.3 | 93.8 | 97.8 | 93.8 | 95.9 | [7 empty] | 0.92 | 1 | [21 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2012-04-16 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SN12MA, 1+n parallel redundant - SMS_03272013174356_6236086
2177856 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SR11MA, 1+1 Redundant - SMS |  | Ac-output UPS | Static | 40SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 5770 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 18327.48 | 18287.76 | 92.1 | 93.2 | 94.1 | 96.3 | 94.2 | 97.3 | 93.8 | 97.7 | 93.6 | 95.8 | [7 empty] | 0.92 | 1 | [21 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP; HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2011-11-10 | 2013-03-25 | United States, Canada | ES_1105798_LIEBERT CORP (96037) ¦ 40SR11MA, 1+1 Redundant - SMS_03272013151928_7568784
2181669 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40MM80MA, Multi-Module MM |  | Ac-output UPS | Static | 40SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 4675 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 14218.64 | 14208.44 | 91.7 | 94.3 | 93.8 | 97.5 | 94.1 | 98.6 | 93.9 | 99.2 | 93.4 | 97 | [7 empty] | 0.92 | 0.99 | [21 empty] | 93.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2013-02-22 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ 40MM80MA, Multi-Module MM_05022013132631_1191297
2181670 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SA80MA, Single Module - SMS |  | Ac-output UPS | Static | 40SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 4675 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 14218.64 | 14208.44 | 91.7 | 94.3 | 93.8 | 97.5 | 94.1 | 98.6 | 93.9 | 99.2 | 93.4 | 97 | [7 empty] | 0.92 | 0.99 | [21 empty] | 93.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2013-02-22 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ 40SA80MA, Single Module - SMS_05022013132613_1173227
2181671 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SN80MA, 1+n parallel redundant - SMS |  | Ac-output UPS | Static | 40SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 4675 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 14218.64 | 14208.44 | 91.7 | 94.3 | 93.8 | 97.5 | 94.1 | 98.6 | 93.9 | 99.2 | 93.4 | 97 | [7 empty] | 0.92 | 0.99 | [21 empty] | 93.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2013-02-22 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ 40SN80MA, 1+n parallel redundant - SMS_05022013132533_1133017
2181672 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SR80MA, 1+1 Redundant - SMS |  | Ac-output UPS | Static | 40SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 4675 | 1150 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 277 | 60 | 14218.64 | 14208.44 | 91.7 | 94.3 | 93.8 | 97.5 | 94.1 | 98.6 | 93.9 | 99.2 | 93.4 | 97 | [7 empty] | 0.92 | 0.99 | [21 empty] | 93.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2013-02-22 | 2013-03-18 | United States, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ 40SR80MA, 1+1 Redundant - SMS_05022013132550_1150496
2192774 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS1 Series | bcdefghijk;b=1/A;c=A-D/N;d=0/1;e=N,R,B,F;f=XXandXcanBeAnyLetter/digit;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXXandXcanBeAanyLetter/digit |  | Ac-output UPS | Static | AS1A1NCUDNNX000 | 4500 | 5000 | AS1C1NCWDNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 16 | 695 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.4 |  | 87.4 |  | 91.7 |  | 92.9 |  | 93.4 |  | 92.7 | [8 empty] | 0.91 |  | 242 |  | 88.8 |  | 92.3 |  | 93.2 |  | 93.6 |  | 91.7 | [8 empty] | 0.94 | 0.94 | 92.7 | AS1A1NCUDNNX000, AS1C1NCWDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ bcdefghijk1_10222013183838_7118540
2192775 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS2 Series | bcdefghijk;b=2/B;c=A-D/N;d=0/1;e=N,R,B,F;f=XXandXcanBeAnyLetter/digit;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D; j=X,Y,S,T;k=XXXandXcanBeAnyLetter/digit |  | Ac-output UPS | Static | AS2A1NCUDNNX000 | 4500 | 5000 | AS2D1NCXDNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.6 |  | 87.5 |  | 91.5 |  | 92.6 |  | 93.1 |  | 92.4 | [8 empty] | 0.91 |  | 309.3 |  | 89.1 |  | 92.5 |  | 93.3 |  | 93.6 |  | 91.9 | [8 empty] | 0.95 | 0.95 | 92.4 | AS2A1NCUDNNX000, AS2D1NCXDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ bcdefghijk2_10222013183931_7171522
2192776 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS6 Series | bcdefghijk; b=6/F;c=A-D/N;d=0/1;e=N,R,B,F;f=XXandXcanBeAnyLetter/digit;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXXandXcanBeAnyLetter/digit |  | Ac-output UPS | Static | AS6A1NCUGNNX000 | 4500 | 5000 | AS6D1NCXGNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 125.5 |  | 86.3 |  | 90.3 |  | 90.8 |  | 90.8 |  | 90.6 | [8 empty] | 0.99 |  | 403 |  | 88.5 |  | 91.1 |  | 91.3 |  | 91 |  | 90.5 | [8 empty] | 0.99 | 0.99 | 90.6 | AS6A1NCUGNNX000, AS6D1NCXGNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ bcdefghijk6_10222013184017_7217157
2193660 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS3 Series | ASbcdefghijk;b=3/C;c=B,C/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS3B1NCVDNNX000 | 9000 | 10000 | AS3C1NCWDNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 100-240 | 50-60 | Yes | 24 | 1060 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 271.08 |  | 86.5 |  | 90.9 |  | 91.6 |  | 91.9 |  | 91.5 | [8 empty] | 0.98 |  | 324.88 |  | 88.3 |  | 91.4 |  | 92 |  | 92 |  | 90.8 | [8 empty] | 0.99 | 0.99 | 91.5 | AS3B1NCVDNNX000 AS3C1NCWDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk3_10312013191939_7179624
2193661 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS4 Series | ASbcdefghijk;b=4/D;c=B-D/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS4B1NCVDNNX000 | 9000 | 10000 | AS4D1NCXDNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 100-240 | 50-60 | No |  | 1240 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 278.53 |  | 86 |  | 90.3 |  | 91.3 |  | 91.6 |  | 91.1 | [8 empty] | 0.99 |  | 414.4 |  | 88.1 |  | 91.3 |  | 91.7 |  | 91.7 |  | 90.6 | [8 empty] | 0.98 | 0.98 | 91.1 | AS4B1NCVDNNX000 AS4D1NCXDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk4_10312013192108_7268318
2193662 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS5 Series | ASbcdefghijk;b=5/E;c=A-C/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS5A1NCUGNNX000 | 4500 | 5000 | AS5C1NCWGNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 16 | 695 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 134.06 |  | 86.1 |  | 89.9 |  | 90.6 |  | 90.6 |  | 90.4 | [8 empty] | 0.99 |  | 304.84 |  | 87.9 |  | 90.7 |  | 91.1 |  | 90.9 |  | 90.1 | [8 empty] | 0.99 | 0.99 | 90.4 | AS5A1NCUGNNX000 AS5C1NCWGNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk5_10312013192437_7477540
2195238 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS1 Series | ASbcdefghijk;b=1/A;c=A-C/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS1A1NCUDNNX000 | 4500 | 5000 | AS1C1NCWDNNX000 | 13500 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 16 | 695 | 440 | 800 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.4 |  | 87.4 |  | 91.7 |  | 92.9 |  | 93.4 |  | 92.7 | [8 empty] | 0.91 |  | 242 |  | 88.8 |  | 92.3 |  | 93.2 |  | 93.6 |  | 91.7 | [8 empty] | 0.94 | 0.94 | 92.7 | AS1A1NCUDNNX000, AS1C1NCWDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk1_10312013175539_2139598
2195239 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS2 Series | ASbcdefghijk;b=2/B;c=A-D/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS2A1NCUDNNX000 | 4500 | 5000 | AS2D1NCXDNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 28.6 |  | 87.5 |  | 91.5 |  | 92.6 |  | 93.1 |  | 92.4 | [8 empty] | 0.91 |  | 309.3 |  | 89.1 |  | 92.5 |  | 93.3 |  | 93.6 |  | 91.9 | [8 empty] | 0.95 | 0.95 | 92.4 | AS2A1NCUDNNX000, AS2D1NCXDNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk2_10312013175729_2249136
2195240 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert APS AS6 Series | ASbcdefghijk;b=6/F;c=A-D/N;d=0/1;e=N,R,B,F;f=XX;g=A-H,J-N,P-U/W;h=N,1-9,A-D;i=N,1-9,A-D;j=X,Y,S,T;k=XXX and X in f and k canBeAnyLetter/digit |  | Ac-output UPS | Static | AS6A1NCUGNNX000 | 4500 | 5000 | AS6D1NCXGNNX000 | 18000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-127 | 50-60 | 100-127 | 50-60 | Yes | 22 | 970 | 440 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 125.5 |  | 86.3 |  | 90.3 |  | 90.8 |  | 90.8 |  | 90.6 | [8 empty] | 0.99 |  | 403 |  | 88.5 |  | 91.1 |  | 91.3 |  | 91 |  | 90.5 | [8 empty] | 0.99 | 0.99 | 90.6 | AS6A1NCUGNNX000, AS6D1NCXGNNX000 | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 5 | 12 | 2 year warranty | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx |  | Serial Port,USB Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/NetworkUPS/Pages/Liebert-APS-On-line-UPS-5-20-kVA.aspx | N/A | 2013-09-12 | 2013-10-17 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (XIAN) CO LTD (647004) ¦ ASbcdefghijk6_10312013180014_2414213
2195473 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-700RT120B | GXT4-700RT120B |  | Ac-output UPS | Static | GXT4-700RT120 | 630 | 700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.58 |  | 81.1 |  | 87.1 |  | 88.6 |  | 88.8 |  | 88.2 | [8 empty] | 0.99 | [22 empty] | 88.2 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 11 | 27 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-700RT120B_11252013011314_1994709
2195778 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-700RT120 | GXT4-700RT120 |  | Ac-output UPS | Static | GXT4-700RT120 | 630 | 700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 25.58 |  | 81.1 |  | 87.1 |  | 88.6 |  | 88.8 |  | 88.2 | [8 empty] | 0.99 | [22 empty] | 88.2 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 11 | 27 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-700RT120_11252013010332_1412224
2195781 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT120 | GXT4-3000RT120 |  | Ac-output UPS | Static | GXT4-3000RT120 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 602 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 62.47 |  | 87.7 |  | 90.5 |  | 90.6 |  | 89.9 |  | 89.3 | [8 empty] | 0.99 | [22 empty] | 89.3 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 3 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT120_11252013012131_2491759
2195782 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT120B | GXT4-1500RT120B |  | Ac-output UPS | Static | GXT4-1500RT120 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.4 |  | 84.9 |  | 89.1 |  | 89.9 |  | 89.8 |  | 88.6 | [8 empty] | 0.99 | [22 empty] | 88.6 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT120B_11252013011501_2101837
2195783 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT120B | GXT4-1000RT120B |  | Ac-output UPS | Static | GXT4-1000RT120 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 26.49 |  | 86.1 |  | 89.5 |  | 90 |  | 89.6 |  | 89.8 | [8 empty] | 0.99 | [22 empty] | 89.8 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT120B_11252013011417_2057705
2195785 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT120 | GXT4-1000RT120 |  | Ac-output UPS | Static | GXT4-1000RT120 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 26.49 |  | 86.1 |  | 89.5 |  | 90 |  | 89.6 |  | 89.8 | [8 empty] | 0.99 | [22 empty] | 89.8 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT120_11252013011401_2041666
2195792 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT120 | GXT4-1500RT120 |  | Ac-output UPS | Static | GXT4-1500RT120 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.4 |  | 84.9 |  | 89.1 |  | 89.9 |  | 89.8 |  | 88.6 | [8 empty] | 0.99 | [22 empty] | 88.6 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT120_11252013011442_2082129
2195794 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT120 | GXT4-2000RT120 |  | Ac-output UPS | Static | GXT4-2000RT120 | 1746 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.91 |  | 87.1 |  | 90 |  | 90.2 |  | 89.7 |  | 90 | [8 empty] | 0.99 | [22 empty] | 90 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 3 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT120_11252013012059_2459396
2195797 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT120B | GXT4-2000RT120B |  | Ac-output UPS | Static | GXT4-2000RT120 | 1746 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 497 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.91 |  | 87.1 |  | 90 |  | 90.2 |  | 89.7 |  | 90 | [8 empty] | 0.99 | [22 empty] | 90 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 3 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT120B_11252013012116_2476180
2195799 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT120B | GXT4-3000RT120B |  | Ac-output UPS | Static | GXT4-3000RT120 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-120 | 50-60 | 110-120 | 50-60 | Yes | 2 | 85 | 430 | 602 | 6 |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 62.47 |  | 87.7 |  | 90.5 |  | 90.6 |  | 89.9 |  | 89.3 | [8 empty] | 0.99 | [22 empty] | 89.3 | N/A | Battery | Vented Lead-acid Battery | Integral | No | 3 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-20 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT120B_11252013012150_2510721
2197242 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT230B | GXT4-1000RT230B |  | Ac-output UPS | Static | GXT4-1000RT230 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.46 |  | 84.6 |  | 89.1 |  | 89.9 |  | 89.6 |  | 89.6 | [8 empty] | 0.99 | [22 empty] | 89.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT230B_11292013035431_7271908
2197243 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT230 | GXT4-1500RT230 |  | Ac-output UPS | Static | GXT4-1500RT230 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.19 |  | 83.9 |  | 89 |  | 90.5 |  | 90.8 |  | 90.2 | [8 empty] | 0.99 | [22 empty] | 90.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT230_11292013035634_7394707
2197244 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT230A | GXT4-1500RT230A |  | Ac-output UPS | Static | GXT4-1500RT230 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.19 |  | 83.9 |  | 89 |  | 90.5 |  | 90.8 |  | 90.2 | [8 empty] | 0.99 | [22 empty] | 90.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT230A_11292013035657_7417766
2197245 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT230E | GXT4-1500RT230E |  | Ac-output UPS | Static | GXT4-1500RT230 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.19 |  | 83.9 |  | 89 |  | 90.5 |  | 90.8 |  | 90.2 | [8 empty] | 0.99 | [22 empty] | 90.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT230E_11292013035749_7469378
2197246 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT230A | GXT4-2000RT230A |  | Ac-output UPS | Static | GXT4-2000RT230 | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.72 |  | 86.2 |  | 90.4 |  | 91.2 |  | 91.1 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT230A_11292013035014_7014821
2197247 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT230E | GXT4-2000RT230E |  | Ac-output UPS | Static | GXT4-2000RT230 | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.72 |  | 86.2 |  | 90.4 |  | 91.2 |  | 91.1 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT230E_11292013035108_7068629
2197248 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT230A | GXT4-3000RT230A |  | Ac-output UPS | Static | GXT4-3000RT230B | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 58.97 |  | 87.6 |  | 90.9 |  | 91.4 |  | 91.3 |  | 91.2 | [8 empty] | 0.99 | [22 empty] | 91.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT230A_11292013034350_6630263
2197249 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT230B | GXT4-3000RT230B |  | Ac-output UPS | Static | GXT4-3000RT230B | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 58.97 |  | 87.6 |  | 90.9 |  | 91.4 |  | 91.3 |  | 91.2 | [8 empty] | 0.99 | [22 empty] | 91.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT230B_11292013034417_6657119
2197250 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-700RT230 | GXT4-700RT230 |  | Ac-output UPS | Static | GXT4-700RT230 | 630 | 700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.61 |  | 81.8 |  | 87.5 |  | 89.3 |  | 89.9 |  | 88.9 | [8 empty] | 0.99 | [22 empty] | 88.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 6 | 27 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-700RT230_11292013035523_7323385
2197251 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-700RT230E | GXT4-700RT230E |  | Ac-output UPS | Static | GXT4-700RT230 | 630 | 700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.61 |  | 81.8 |  | 87.5 |  | 89.3 |  | 89.9 |  | 88.9 | [8 empty] | 0.99 | [22 empty] | 88.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 6 | 27 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-700RT230E_11292013035611_7371242
2197252 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT230 | GXT4-1000RT230 |  | Ac-output UPS | Static | GXT4-1000RT230 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.46 |  | 84.6 |  | 89.1 |  | 89.9 |  | 89.6 |  | 89.6 | [8 empty] | 0.99 | [22 empty] | 89.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT230_11292013035337_7217052
2197253 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT230A | GXT4-1000RT230A |  | Ac-output UPS | Static | GXT4-1000RT230 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.46 |  | 84.6 |  | 89.1 |  | 89.9 |  | 89.6 |  | 89.6 | [8 empty] | 0.99 | [22 empty] | 89.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT230A_11292013035401_7241579
2197254 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1000RT230E | GXT4-1000RT230E |  | Ac-output UPS | Static | GXT4-1000RT230 | 900 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.46 |  | 84.6 |  | 89.1 |  | 89.9 |  | 89.6 |  | 89.6 | [8 empty] | 0.99 | [22 empty] | 89.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1000RT230E_11292013035458_7298712
2197255 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-1500RT230B | GXT4-1500RT230B |  | Ac-output UPS | Static | GXT4-1500RT230 | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.19 |  | 83.9 |  | 89 |  | 90.5 |  | 90.8 |  | 90.2 | [8 empty] | 0.99 | [22 empty] | 90.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-1500RT230B_11292013035722_7442913
2197256 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT230B | GXT4-2000RT230B |  | Ac-output UPS | Static | GXT4-2000RT230 | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.72 |  | 86.2 |  | 90.4 |  | 91.2 |  | 91.1 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT230B_11292013035041_7041370
2197257 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT208 | GXT4-3000RT208 |  | Ac-output UPS | Static | GXT4-3000RT208 | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-208 | 50-60 | 208-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 240 | 60 | 61.47 |  | 87 |  | 90.3 |  | 90.7 |  | 90.5 |  | 90.5 | [8 empty] | 0.99 | [22 empty] | 90.5 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT208_11292013034047_6447237
2197258 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT230 | GXT4-3000RT230 |  | Ac-output UPS | Static | GXT4-3000RT230B | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 58.97 |  | 87.6 |  | 90.9 |  | 91.4 |  | 91.3 |  | 91.2 | [8 empty] | 0.99 | [22 empty] | 91.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT230_11292013034240_6560790
2197259 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-3000RT230E | GXT4-3000RT230E |  | Ac-output UPS | Static | GXT4-3000RT230B | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 602 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 58.97 |  | 87.6 |  | 90.9 |  | 91.4 |  | 91.3 |  | 91.2 | [8 empty] | 0.99 | [22 empty] | 91.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-3000RT230E_11292013034448_6688165
2197260 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-700RT230B | GXT4-700RT230B |  | Ac-output UPS | Static | GXT4-700RT230 | 630 | 700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 27.61 |  | 81.8 |  | 87.5 |  | 89.3 |  | 89.9 |  | 88.9 | [8 empty] | 0.99 | [22 empty] | 88.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 6 | 27 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-700RT230B_11292013035547_7347361
2197261 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-2000RT230 | GXT4-2000RT230 |  | Ac-output UPS | Static | GXT4-2000RT230 | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 85 | 430 | 497 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 46.72 |  | 86.2 |  | 90.4 |  | 91.2 |  | 91.1 |  | 90.9 | [8 empty] | 0.99 | [22 empty] | 90.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 11 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-18 | 2013-11-28 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-2000RT230_11292013062336_6216751
2204628 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-10000RT208 | GXT4-10000RT208 |  | Ac-output UPS | Static | GXT4-10000RT208 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-240 | 50-60 | 200-240 | 50-60 | Yes |  | 261 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 129.83 |  | 90.8 |  | 92 |  | 91.8 |  | 91.2 |  | 91.7 | [8 empty] | 0.99 | [22 empty] | 91.7 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-10000RT208_02182014103023_9423174
2204629 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-10000RT230 | GXT4-10000RT230 |  | Ac-output UPS | Static | GXT4-10000RT230 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 261 | 430 | 581 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 112.58 |  | 91.3 |  | 93.1 |  | 93.3 |  | 93.1 |  | 93.2 | [8 empty] | 0.99 | [22 empty] | 93.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 10 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-10000RT230_02182014103159_9519099
2204630 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-10000RT230E | GXT4-10000RT230E |  | Ac-output UPS | Static | GXT4-10000RT230 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 261 | 430 | 581 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 112.58 |  | 91.3 |  | 93.1 |  | 93.3 |  | 93.1 |  | 93.2 | [8 empty] | 0.99 | [22 empty] | 93.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 4 | 10 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-10000RT230E_02182014103251_9571311
2204631 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-5000RT208 | GXT4-5000RT208 |  | Ac-output UPS | Static | GXT4-5000RT208 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 77.68 |  | 88.8 |  | 91.9 |  | 92.6 |  | 92 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-5000RT208_02182014103313_9593103
2204632 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-5000RT230 | GXT4-5000RT230 |  | Ac-output UPS | Static | GXT4-5000RT230 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.2 |  | 90.1 |  | 93 |  | 93.7 |  | 94 |  | 93.6 | [8 empty] | 0.99 | [22 empty] | 93.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 9 | 22 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-5000RT230_02182014103333_9613460
2204633 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-5000RT230E | GXT4-5000RT230E |  | Ac-output UPS | Static | GXT4-5000RT230 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.2 |  | 90.1 |  | 93 |  | 93.7 |  | 94 |  | 93.6 | [8 empty] | 0.99 | [22 empty] | 93.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 9 | 22 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-5000RT230E_02182014103357_9637438
2204634 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-5000RT230U | GXT4-5000RT230U |  | Ac-output UPS | Static | GXT4-5000RT230 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.2 |  | 90.1 |  | 93 |  | 93.7 |  | 94 |  | 93.6 | [8 empty] | 0.99 | [22 empty] | 93.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 9 | 22 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-5000RT230U_02182014103433_9673236
2204635 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-6000RT208 | GXT4-6000RT208 |  | Ac-output UPS | Static | GXT4-6000RT208 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 76.56 |  | 90.2 |  | 92.5 |  | 92.9 |  | 92.7 |  | 92.7 | [8 empty] | 0.99 | [22 empty] | 92.7 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5 | 12 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-6000RT208_02182014103454_9694959
2204636 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-6000RT230 | GXT4-6000RT230 |  | Ac-output UPS | Static | GXT4-6000RT230 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.24 |  | 91 |  | 93.4 |  | 93.9 |  | 93.9 |  | 93.8 | [8 empty] | 0.99 | [22 empty] | 93.8 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-6000RT230_02182014102935_9375437
2204637 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-6000RT230E | GXT4-6000RT230E |  | Ac-output UPS | Static | GXT4-6000RT230 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.24 |  | 91 |  | 93.4 |  | 93.9 |  | 93.9 |  | 93.8 | [8 empty] | 0.99 | [22 empty] | 93.8 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-6000RT230E_02182014103537_9737455
2204638 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-6000RTL630 | GXT4-6000RTL630 |  | Ac-output UPS | Static | GXT4-6000RTL630 | 4200 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 82.67 |  | 89.5 |  | 92.4 |  | 93.1 |  | 93.2 |  | 92.9 | [8 empty] | 0.99 | [22 empty] | 92.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 8 | 20 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-6000RTL630_02182014103558_9758814
2204639 | Vertiv Corporation | EMERSON NETWORK POWER | GXT4-8000RT208 | GXT4-8000RT208 |  | Ac-output UPS | Static | GXT4-8000RT208 | 7200 | 8000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-240 | 50-60 | 200-240 | 50-60 | Yes |  | 261 | 430 | 662 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 128.62 |  | 89.4 |  | 91.7 |  | 92 |  | 91.7 |  | 91.8 | [8 empty] | 0.99 | [22 empty] | 91.8 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 8 | 20 | 2 | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | http://www.emersonnetworkpower.com/EN-US/PRODUCTS/ACPOWER/Pages/default.aspx | N/A | 2014-03-31 | 2014-01-27 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_EMERSON NETWORK POWER (679972) ¦ GXT4-8000RT208_02182014103619_9779669
2209493 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40MM40AB0B |  | Ac-output UPS | Static | 40SN40ABBB | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 600-600 | 60-60 | 600-600 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 600 | 60 | 600 | 60 | 17073.6 |  | 90.8 |  | 93.2 |  | 93.7 |  | 93.5 |  | 92.7 | [8 empty] | 0.92 | [22 empty] | 92.7 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40MM40AB0B_02182014011931_6371169
2209494 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SA40A333 |  | Ac-output UPS | Static | 40SN40A333 | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 575-575 | 60-60 | 575-575 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 575 | 60 | 575 | 60 | 17271.6 |  | 90.6 |  | 93.3 |  | 93.7 |  | 93.4 |  | 92.8 | [8 empty] | 0.92 | [22 empty] | 92.8 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SA40A333_02182014011857_6337199
2209495 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SA40ABBB |  | Ac-output UPS | Static | 40SN40ABBB | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 600-600 | 60-60 | 600-600 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 600 | 60 | 600 | 60 | 17073.6 |  | 90.8 |  | 93.2 |  | 93.7 |  | 93.5 |  | 92.7 | [8 empty] | 0.92 | [22 empty] | 92.7 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SA40ABBB_02182014012000_6400985
2209496 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SN40A333 |  | Ac-output UPS | Static | 40SN40A333 | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 575-575 | 60-60 | 575-575 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 575 | 60 | 575 | 60 | 17271.6 |  | 90.6 |  | 93.3 |  | 93.7 |  | 93.4 |  | 92.8 | [8 empty] | 0.92 | [22 empty] | 92.8 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SN40A333_02182014011831_6311859
2209497 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SN40ABBB |  | Ac-output UPS | Static | 40SN40ABBB | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 600-600 | 60-60 | 600-600 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 600 | 60 | 600 | 60 | 17073.6 |  | 90.8 |  | 93.2 |  | 93.7 |  | 93.5 |  | 92.7 | [8 empty] | 0.92 | [22 empty] | 92.7 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SN40ABBB_02182014012044_6444691
2209498 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SR40A333 |  | Ac-output UPS | Static | 40SN40A333 | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 575-575 | 60-60 | 575-575 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 575 | 60 | 575 | 60 | 17271.6 |  | 90.6 |  | 93.3 |  | 93.7 |  | 93.4 |  | 92.8 | [8 empty] | 0.92 | [22 empty] | 92.8 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SR40A333_02182014011842_6322920
2209499 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40SR40ABBB |  | Ac-output UPS | Static | 40SN40ABBB | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 600-600 | 60-60 | 600-600 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 600 | 60 | 600 | 60 | 17073.6 |  | 90.8 |  | 93.2 |  | 93.7 |  | 93.5 |  | 92.7 | [8 empty] | 0.92 | [22 empty] | 92.7 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40SR40ABBB_02182014011948_6388548
2209500 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert NXL | 40MM40A303 |  | Ac-output UPS | Static | 40SN40A333 | 360000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 575-575 | 60-60 | 575-575 | 60-60 | No |  | 1950 | 2515 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 575 | 60 | 575 | 60 | 17271.6 |  | 90.6 |  | 93.3 |  | 93.7 |  | 93.4 |  | 92.8 | [8 empty] | 0.92 | [22 empty] | 92.8 | N/A | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNXLOnLineUPS250750kVA.aspx | N/A | 2014-04-01 | 2014-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1105798_Liebert Corp (260123) ¦ 40MM40A303_02182014011913_6353493
2219685 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | (e=0,1,2 or 3; f=C or Y; g=0, F, H, M, G or L; h=0 or 1) | Liebert eXM,47SA015A(e)(f)(g)(h),; Liebert eXM,47SA020A(e)(f)(g)(h),; Liebert eXM,47SA030A(e)(f)(g)(h),; Liebert eXM,47SA040A(e)(f)(g)(h), | Ac-output UPS | Static | 47SA010A0C00 | 10000 | 10000 | 47SA040A0C00 | 40000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 60-60 | 208-220 | 60-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 265.4 | 0 | 89.3 | 0 | 93.1 | 0 | 94.4 | 0 | 94.8 | 0 | 94.2 | 0 | [7 empty] | 0.99 | 0 | 434.7 | 0 | 94.1 | 0 | 95.4 | 0 | 95.3 | 0 | 94.8 | 0 | 95 | 0 | [7 empty] | 0.99 | 0.99 | 94.2 | Power Module, eXM 20KVA. | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 17 minutes | 34 minutes | 1 yr | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,HTTPS,HTTP,Modbus RTU | YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2014-08-06 | 2014-08-14 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_47SA010A0C00_08182014014743_6463338
2219686 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | (e=0,1,2 or 3; f=C or Y; g=0, F, H, M, G or L; h=0 or 1) | Liebert eXM,47SA080A(e)(f)(g)(h),; Liebert eXM,47SA100A(e)(f)(g)(h), | Ac-output UPS | Static | 47SA060A0C00 | 60000 | 60000 | 47SA100A0C00 | 100000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 60-60 | 208-220 | 60-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 654.2 | 0 | 93.9 | 0 | 95.3 | 0 | 95.2 | 0 | 94.7 | 0 | 94.9 | 0 | [7 empty] | 0.99 | 0 | 988.8 | 0 | 94.3 | 0 | 95.5 | 0 | 95.3 | 0 | 94.7 | 0 | 95.1 | 0 | [7 empty] | 0.99 | 0.99 | 94.9 | Power Module, eXM 20KVA. | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 minutes | 20 minutes | 1 yr | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,HTTPS,HTTP,Modbus RTU | YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2014-08-06 | 2014-08-14 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_47SA060A0C00_08182014014852_6532814
2233128 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 47SA120A(e)(f)(g)(h) | Liebert eXM,47SA120A(e)(f)(g)(h),; Liebert eXM,47SA140A(e)(f)(g)(h),; Liebert eXM,47SA160A(e)(f)(g)(h),; Liebert eXM,47SA180A(e)(f)(g)(h),; Liebert eXM,47SA200A(e)(f)(g)(h), | Ac-output UPS | Static | 47SA120A(e)(f)(g)(h) | 120000 | 120000 | 47SA200A(e)(f)(g)(h) | 200000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1990 | 888 | 993 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 1341.73 |  | 94 |  | 95.3 |  | 95.2 |  | 94.8 |  | 94.9 | [8 empty] | 1 |  | 2208.24 |  | 93.7 |  | 95.1 |  | 95 |  | 94.7 |  | 94.7 | [8 empty] | 0.99 | 0.99 | 94.9 | 47SA120A(e)(f)(g)(h), 47SA200A(e)(f)(g)(h) | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-03-01 | 2015-02-13 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_47SA120A(e)(f)(g)(h)_02142015051752_1072937
2238856 | Vertiv Corporation | EMERSON NETWORK POWER | NX Series | 38SA400AAA | ,38SA400A0A,; ,38SN400A0A,; ,38SN400AAA,; NX Series,38SA400AAA, | Ac-output UPS | Static | 38SA400A0A | 400000 | 400000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2300 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 5876.84 | 4876.76 | 92.8 | 95.2 | 94.9 | 97.4 | 95.4 | 98.1 | 95.4 | 98.4 | 94.5 | 97 | [7 empty] | 0.99 | 0.97 | [21 empty] | 94.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNX-225-600kVAkWUPS.aspx | N/A | 2012-07-19 | 2015-05-07 | United States, Canada | ES_1097807_38SA400AAA_05072015180729_2049834
2238857 | Vertiv Corporation | EMERSON NETWORK POWER | NX Series | 38SA500AAA | ,38SA500A0A,; ,38SN500A0A,; ,38SN500AAA,; NX Series,38SA500AAA, | Ac-output UPS | Static | 38SA500A0A | 500000 | 500000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2300 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 5876.84 | 4876.76 | 93.6 | 96 | 95.2 | 97.8 | 95.4 | 98.3 | 95.1 | 98.6 | 94.8 | 97.5 | [7 empty] | 0.99 | 0.98 | [21 empty] | 94.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 10 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNX-225-600kVAkWUPS.aspx | N/A | 2012-07-19 | 2015-05-07 | United States, Canada | ES_1097807_38SA500AAA_05072015180215_1735958
2238858 | Vertiv Corporation | EMERSON NETWORK POWER | NX Series | 38SA600AAA | ,38SA600A0A,; ,38SN600A0A,; ,38SN600AAA,; NX Series,38SA600AAA, | Ac-output UPS | Static | 38SA600A0A | 600000 | 600000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2300 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 5876.84 | 4876.76 | 94.2 | 96.6 | 95.4 | 98.1 | 95.2 | 98.5 | 94.6 | 98.7 | 95.1 | 97.8 | [7 empty] | 0.99 | 0.99 | [21 empty] | 95.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNX-225-600kVAkWUPS.aspx | N/A | 2012-07-19 | 2015-05-07 | United States, Canada | ES_1097807_38SA600AAA_05072015180809_2089884
2240341 | Vertiv Corporation | EMERSON NETWORK POWER | NX Series | 38SA300A0A | ,38SA300AAA,; ,38SN300A0A,; ,38SN300AAA,; NX Series,38SA300A0A, | Ac-output UPS | Static | 38SA300A0A | 300000 | 300000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 1356 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 3227.8 | 2749.6 | 93.9 | 96.3 | 95.2 | 97.8 | 95.3 | 98.3 | 95 | 98.6 | 94.9 | 97.6 | [7 empty] | 0.99 | 0.99 | [21 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNX-225-600kVAkWUPS.aspx | N/A | 2012-07-19 | 2015-05-28 | United States, Canada | ES_1097807_38SA300A0A_05282015183228_7948131
2240343 | Vertiv Corporation | EMERSON NETWORK POWER | NX Series | 38SA250A0A | ,38SA225A0A,; ,38SA225AAA,; ,38SA250AAA,; ,38SN225A0A,; ,38SN225AAA,; ,38SN250A0A,; ,38SN250AAA,; NX Series,38SA250A0A, | Ac-output UPS | Static | 38SA250A0A | 250000 | 250000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 1356 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 3227.8 | 2749.5 | 93.1 | 95.5 | 95.1 | 97.6 | 95.3 | 98.2 | 95.2 | 98.5 | 94.6 | 97.2 | [7 empty] | 0.99 | 0.99 | [21 empty] | 94.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/LargeFacilityUPS/Pages/LiebertNX-225-600kVAkWUPS.aspx | N/A | 2012-07-19 | 2015-05-28 | United States, Canada | ES_1097807_38SA250A0A_05282015194754_2474028
2259868 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0120kTK16FN01000 | Liebert eXM,eXM 0080kTK16FN01000,; Liebert eXM,eXM 0100kTK16FN01000,; Liebert eXM,eXM 0120kTK16FN01000, | Ac-output UPS | Static | eXM 0080kTK16FN01000 | 80000 | 80000 | eXM 0120kTK16FN01000 | 120000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 512.72 |  | 95.5 |  | 96.2 |  | 95.8 |  | 95.5 |  | 95.9 | [8 empty] | 0.99 |  | 753.63 |  | 95.7 |  | 96.3 |  | 96.1 |  | 95.7 |  | 96.1 | [8 empty] | 0.99 | 0.99 | 95.9 | PM40 | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0120kTK16FN01000_01072016082135_4895583
2259869 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0120kTK16FN01000 | Liebert eXM,eXM 0080kTK16FN01000,; Liebert eXM,eXM 0100kTK16FN01000,; Liebert eXM,eXM 0120kTK16FN01000, | Ac-output UPS | Static | eXM 0080kTK16FN01000 | 80000 | 80000 | eXM 0120kTK16FN01000 | 120000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 512.72 |  | 95.5 |  | 96.2 |  | 95.8 |  | 95.5 |  | 95.9 | [8 empty] | 0.99 |  | 753.63 |  | 95.7 |  | 96.3 |  | 96.1 |  | 95.7 |  | 96.1 | [8 empty] | 0.99 | 0.99 | 95.9 | PM40 | Other | Flywheel | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0120kTK16FN01000_01072016082333_5013114
2259870 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0120kTK16FN01000 | Liebert eXM,eXM 0080kTK16FN01000,; Liebert eXM,eXM 0100kTK16FN01000,; Liebert eXM,eXM 0120kTK16FN01000, | Ac-output UPS | Static | eXM 0080kTK16FN01000 | 80000 | 80000 | eXM 0120kTK16FN01000 | 120000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 512.72 |  | 95.5 |  | 96.2 |  | 95.8 |  | 95.5 |  | 95.9 | [8 empty] | 0.99 |  | 753.63 |  | 95.7 |  | 96.3 |  | 96.1 |  | 95.7 |  | 96.1 | [8 empty] | 0.99 | 0.99 | 95.9 | PM40 | Other | Vented Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0120kTK16FN01000_01072016082657_5217505
2260150 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0200kTK16FN01000 | Liebert eXM,eXM 0160kTK16FN01000,; Liebert eXM,eXM 0200kTK16FN01000, | Ac-output UPS | Static | eXM 0160kTK16FN01000 | 160000 | 160000 | eXM 0200kTK16FN01000 | 200000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 1018.01 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 |  | 1253.22 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 | 0.99 | 96.2 | PM40 | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0200kTK16FN01000_01072016082819_5299173
2260151 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0200kTK16FN01000 | Liebert eXM,eXM 0160kTK16FN01000,; Liebert eXM,eXM 0200kTK16FN01000, | Ac-output UPS | Static | eXM 0160kTK16FN01000 | 160000 | 160000 | eXM 0200kTK16FN01000 | 200000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 1018.01 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 |  | 1253.22 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 | 0.99 | 96.2 | PM40 | Other | Flywheel | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0200kTK16FN01000_01072016082857_5337775
2260152 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | eXM 0200kTK16FN01000 | Liebert eXM,eXM 0160kTK16FN01000,; Liebert eXM,eXM 0200kTK16FN01000, | Ac-output UPS | Static | eXM 0160kTK16FN01000 | 160000 | 160000 | eXM 0200kTK16FN01000 | 200000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 2000 | 600 | 1000 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 1018.01 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 |  | 1253.22 |  | 95.8 |  | 96.4 |  | 96.1 |  | 95.7 |  | 96.2 | [8 empty] | 0.99 | 0.99 | 96.2 | PM40 | Other | Vented Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | HTTP, HTTPS, YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2015-11-20 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_eXM 0200kTK16FN01000_01072016082945_5385389
2260184 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA200LAA | Liebert eXM,51SA050BAA,; Liebert eXM,51SA100EAA,; Liebert eXM,51SA150HAA,; Liebert eXM,51SN050BAA,; Liebert eXM,51SN100EAA,; Liebert eXM,51SN150HAA,; Liebert eXM,51SN200LAA, | Ac-output UPS | Static | 51SA050BAA | 50000 | 50000 | 51SA200LAA | 200000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 848 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 338.66 |  | 95.9 |  | 96.6 |  | 96.4 |  | 96.2 |  | 96.4 | [8 empty] | 0.99 |  | 1264.16 |  | 96 |  | 96.7 |  | 96.5 |  | 96.2 |  | 96.5 | [8 empty] | 0.99 | 0.99 | 96.4 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | YDN23, HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2016-01-01 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA200LAA_11132015073713_0233805
2260188 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA250NAA | Liebert eXM,51SN250NAA, | Ac-output UPS | Static | 51SA250NAA | 1 | 1 | 51SA250NAA | 250000 |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 848 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 1488.78 |  | 96.2 |  | 96.7 |  | 96.6 |  | 96.2 |  | 96.6 | [8 empty] | 0.99 | 0.99 | 0 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Modbus TCP,Other,SNMP (v1, 2 or 3),Modbus RTU | YFN23, HTTP, HTTPS | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2016-01-01 | 2015-11-12 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA250NAA_11132015073538_0138712
2272040 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMA625A |  | Ac-output UPS | Static | 46SN625A | 625000 | 625000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2620 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.01 | 7052.56 | 94.7 | 95.5 | 96.3 | 97.5 | 96.7 | 98.1 | 96.7 | 98.4 | 96 | 97.1 | [7 empty] | 1 | 1 | [21 empty] | 96 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46MMA625A_07082016180058_0858300
2272041 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNA625A | ,46SAA625A,; ,46SRA625A, | Ac-output UPS | Static | 46SN625A | 625000 | 625000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2835 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.01 | 7052.56 | 94.7 | 95.5 | 96.3 | 97.5 | 96.7 | 98.1 | 96.7 | 98.4 | 96 | 97.1 | [7 empty] | 1 | 1 | [21 empty] | 96 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46SNA625A_07082016175731_0651564
2272042 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMA750A |  | Ac-output UPS | Static | 46SN750A | 750000 | 750000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2620 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.04 | 7052.56 | 95.2 | 96.1 | 96.5 | 97.8 | 96.7 | 98.3 | 96.6 | 98.5 | 96.3 | 97.5 | [7 empty] | 1 | 1 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46MMA750A_07082016181922_1962946
2272044 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNA750A | ,46SAA750A,; ,46SRA750A, | Ac-output UPS | Static | 46SN625A | 750000 | 750000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2835 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.04 | 7052.56 | 95.2 | 96.1 | 96.5 | 97.8 | 96.7 | 98.3 | 96.6 | 98.5 | 96.3 | 97.5 | [7 empty] | 1 | 1 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46SNA750A_07082016181130_1490764
2272060 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMA800A |  | Ac-output UPS | Static | 46SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2620 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.04 | 7052.56 | 95.4 | 96.4 | 96.6 | 97.9 | 96.7 | 98.3 | 96.5 | 98.5 | 96.3 | 97.6 | [7 empty] | 1 | 1 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46MMA800A_07082016194548_7148775
2272061 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNA800A | ,46SAA800A,; ,46SRA800A, | Ac-output UPS | Static | 46SN800A | 800000 | 800000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 2835 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7024.04 | 7052.56 | 95.4 | 96.4 | 96.6 | 97.9 | 96.7 | 98.3 | 96.5 | 98.5 | 96.3 | 97.6 | [7 empty] | 1 | 1 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2014-02-26 | 2016-04-20 | United States, Canada | ES_1097807_46SNA800A_07082016194146_6906597
2272062 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMC10MA |  | Ac-output UPS | Static | 46SN10MA | 1000000 | 1000000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3270 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 94.7 | 95.4 | 96.2 | 97.4 | 96.6 | 97.9 | 96.5 | 98.2 | 95.9 | 97 | [7 empty] | 1 | 1 | [21 empty] | 95.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46MMC10MA_07082016200055_8055996
2272063 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNC10MA | ,46SAC10MA,; ,46SRC10MA, | Ac-output UPS | Static | 46SN10MA | 1000000 | 1000000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3978 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 94.7 | 95.4 | 96.2 | 97.4 | 96.6 | 97.9 | 96.5 | 98.2 | 95.9 | 97 | [7 empty] | 1 | 1 | [21 empty] | 95.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46SNC10MA_07082016195815_7895694
2272064 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMC11MA |  | Ac-output UPS | Static | 46SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3270 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 95 | 95.8 | 96.4 | 97.5 | 96.6 | 98 | 96.4 | 98.2 | 96.1 | 97.2 | [7 empty] | 1 | 1 | [21 empty] | 96.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46MMC11MA_07082016201333_8813237
2272065 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNC11MA | ,46SAC11MA,; ,46SRC11MA, | Ac-output UPS | Static | 46SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3978 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 95 | 95.8 | 96.4 | 97.5 | 96.6 | 98 | 96.4 | 98.2 | 96.1 | 97.2 | [7 empty] | 1 | 1 | [21 empty] | 96.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46SNC11MA_07082016201004_8604780
2272068 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46MMC12MA |  | Ac-output UPS | Static | 46SN12MA | 1200000 | 1200000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3270 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 95.3 | 96.1 | 96.4 | 97.7 | 96.5 | 98.1 | 96.3 | 98.3 | 96.2 | 97.4 | [7 empty] | 1 | 1 | [21 empty] | 96.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46MMC12MA_07082016203002_9802950
2272069 | Vertiv Corporation | EMERSON NETWORK POWER | eXL Series | 46SNC12MA | ,46SAC12MA,; ,46SRC12MA, | Ac-output UPS | Static | 46SN12MA | 1200000 | 1200000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 1950 | 3978 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 10946.56 | 10978.72 | 95.3 | 96.1 | 96.4 | 97.7 | 96.5 | 98.1 | 96.3 | 98.3 | 96.2 | 97.4 | [7 empty] | 1 | 1 | [21 empty] | 96.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | http://www.emersonnetworkpower.com/en-CALA/Products/ACPower/LargeFacilityUPS/Pages/Liebert-eXL-On-Line-UPS-800kVA-kW.aspx | N/A | 2015-05-22 | 2016-06-22 | United States, Canada | ES_1097807_46SNC12MA_07082016202805_9685474
2296442 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA160ARA | Liebert eXM,51SN160ARA, | Ac-output UPS | Static | 51SA160ARA | 40000 | 40000 | 51SA250NAA |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 848 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1267.25 |  | 92.6 |  | 95.4 |  | 96.2 |  | 96.5 |  | 94.9 | [8 empty] | 0.98 | [22 empty] | 94.9 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Other | HTTP, HTTPS YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2017-06-01 | 2017-05-19 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA160ARA_05232017052948_7388756
2296443 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA160AQA | Liebert eXM,51SA160DQA,; Liebert eXM,51SA160DRA,; Liebert eXM,51SA160FQA,; Liebert eXM,51SA160FRA,; Liebert eXM,51SA160JQA,; Liebert eXM,51SA160JRA,; Liebert eXM,51SA175TQA,; Liebert eXM,51SA175TRA,; Liebert eXM,51SA180KQA,; Liebert eXM,51SA180KRA,; Liebert eXM,51SA200BQA,; Liebert eXM,51SA200BRA,; Liebert eXM,51SA200EQA,; Liebert eXM,51SA200ERA,; Liebert eXM,51SA200HQA,; Liebert eXM,51SA200HRA,; Liebert eXM,51SA200LQA,; Liebert eXM,51SA200LRA,; Liebert eXM,51SA225MAA,; Liebert eXM,51SA250BAA,; Liebert eXM,51SA250BBA,; Liebert eXM,51SA250EAA,; Liebert eXM,51SA250EBA,; Liebert eXM,51SA250HAA,; Liebert eXM,51SA250HBA,; Liebert eXM,51SA250LAA,; Liebert eXM,51SA250LBA,; Liebert eXM,51SN160AQA,; Liebert eXM,51SN160DQA,; Liebert eXM,51SN160DRA,; Liebert eXM,51SN160FQA,; Liebert eXM,51SN160FRA,; Liebert eXM,51SN160JQA,; Liebert eXM,51SN160JRA,; Liebert eXM,51SN175TQA,; Liebert eXM,51SN175TRA,; Liebert eXM,51SN180KQA,; Liebert eXM,51SN180KRA,; Liebert eXM,51SN200BQA,; Liebert eXM,51SN200BRA,; Liebert eXM,51SN200EQA,; Liebert eXM,51SN200ERA,; Liebert eXM,51SN200HQA,; Liebert eXM,51SN200HRA,; Liebert eXM,51SN200LQA,; Liebert eXM,51SN200LRA,; Liebert eXM,51SN225MAA,; Liebert eXM,51SN250BAA,; Liebert eXM,51SN250BBA,; Liebert eXM,51SN250EAA,; Liebert eXM,51SN250EBA,; Liebert eXM,51SN250HAA,; Liebert eXM,51SN250HBA,; Liebert eXM,51SN250LAA,; Liebert eXM,51SN250LBA, | Ac-output UPS | Static | 51SA160AQA | 40000 | 40000 | 51SA250NAA |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 848 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1077.64 |  | 94.3 |  | 95.8 |  | 96.2 |  | 96.1 |  | 95.6 | [8 empty] | 0.99 | [22 empty] | 95.6 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Other | HTTP, HTTPS YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2017-06-01 | 2017-05-19 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA160AQA_05232017062205_0525026
2296444 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA030QAA | Liebert eXM,51SN030QAA, | Ac-output UPS | Static | 51SA030QAA | 30000 | 30000 | 51SA200LAA |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 608 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 891.57 |  | 95.5 |  | 96.6 |  | 96.6 |  | 96.7 |  | 96.4 | [8 empty] | 0.98 | [22 empty] | 96.4 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Other | HTTP, HTTPS YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2017-06-01 | 2017-05-19 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA030QAA_05232017070732_3252212
2296445 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert eXM | 51SA030QBA | Liebert eXM,51SA040AAA,; Liebert eXM,51SA040ABA,; Liebert eXM,51SA050BBA,; Liebert eXM,51SA060CAA,; Liebert eXM,51SA060CBA,; Liebert eXM,51SA060QAA,; Liebert eXM,51SA060QBA,; Liebert eXM,51SA075RAA,; Liebert eXM,51SA075RBA,; Liebert eXM,51SA080AAA,; Liebert eXM,51SA080ABA,; Liebert eXM,51SA080DAA,; Liebert eXM,51SA080DBA,; Liebert eXM,51SA100BAA,; Liebert eXM,51SA100BBA,; Liebert eXM,51SA100EBA,; Liebert eXM,51SA120AAA,; Liebert eXM,51SA120ABA,; Liebert eXM,51SA120DAA,; Liebert eXM,51SA120DBA,; Liebert eXM,51SA120FAA,; Liebert eXM,51SA120FBA,; Liebert eXM,51SA125SAA,; Liebert eXM,51SA125SBA,; Liebert eXM,51SA140GAA,; Liebert eXM,51SA140GBA,; Liebert eXM,51SA150BAA,; Liebert eXM,51SA150BBA,; Liebert eXM,51SA150EAA,; Liebert eXM,51SA150EBA,; Liebert eXM,51SA150HBA,; Liebert eXM,51SA160AAA,; Liebert eXM,51SA160ABA,; Liebert eXM,51SA160DAA,; Liebert eXM,51SA160DBA,; Liebert eXM,51SA160FAA,; Liebert eXM,51SA160FBA,; Liebert eXM,51SA160JAA,; Liebert eXM,51SA175TAA,; Liebert eXM,51SA180KAA,; Liebert eXM,51SA200BAA,; Liebert eXM,51SA200BBA,; Liebert eXM,51SA200EAA,; Liebert eXM,51SA200EBA,; Liebert eXM,51SA200HAA,; Liebert eXM,51SA200HBA,; Liebert eXM,51SN030QBA,; Liebert eXM,51SN040AAA,; Liebert eXM,51SN040ABA,; Liebert eXM,51SN050BBA,; Liebert eXM,51SN060CAA,; Liebert eXM,51SN060CBA,; Liebert eXM,51SN060QAA,; Liebert eXM,51SN060QBA,; Liebert eXM,51SN075RAA,; Liebert eXM,51SN075RBA,; Liebert eXM,51SN080AAA,; Liebert eXM,51SN080ABA,; Liebert eXM,51SN080DAA,; Liebert eXM,51SN080DBA,; Liebert eXM,51SN100BAA,; Liebert eXM,51SN100BBA,; Liebert eXM,51SN100EBA,; Liebert eXM,51SN120AAA,; Liebert eXM,51SN120ABA,; Liebert eXM,51SN120DAA,; Liebert eXM,51SN120DBA,; Liebert eXM,51SN120FAA,; Liebert eXM,51SN120FBA,; Liebert eXM,51SN125SAA,; Liebert eXM,51SN125SBA,; Liebert eXM,51SN140GAA,; Liebert eXM,51SN140GBA,; Liebert eXM,51SN150BAA,; Liebert eXM,51SN150BBA,; Liebert eXM,51SN150EAA,; Liebert eXM,51SN150EBA,; Liebert eXM,51SN150HBA,; Liebert eXM,51SN160AAA,; Liebert eXM,51SN160ABA,; Liebert eXM,51SN160DAA,; Liebert eXM,51SN160DBA,; Liebert eXM,51SN160FAA,; Liebert eXM,51SN160FBA,; Liebert eXM,51SN160JAA,; Liebert eXM,51SN175TAA,; Liebert eXM,51SN180KAA,; Liebert eXM,51SN200BAA,; Liebert eXM,51SN200BBA,; Liebert eXM,51SN200EAA,; Liebert eXM,51SN200EBA,; Liebert eXM,51SN200HAA,; Liebert eXM,51SN200HBA, | Ac-output UPS | Static | 51SA030QBA | 30000 | 30000 | 51SA200LAA |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2000 | 608 | 994 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | Yes | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 1092.3 |  | 93.1 |  | 95.6 |  | 96.4 |  | 96.8 |  | 95.2 | [8 empty] | 0.96 | [22 empty] | 95.2 | eXM 50KVA | Other | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port | Other | HTTP, HTTPS YDN23 | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2017-06-01 | 2017-05-19 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_51SA030QBA_05232017095155_3115996
2304964 | Vertiv Corporation | EMERSON NETWORK POWER | Liebert EXS | 0020kTH1AFN01000 | Liebert EXS,0010kTH1AFN01000,; Liebert EXS,0010kTH1AFN02000,; Liebert EXS,0015kTH1AFN01000,; Liebert EXS,0015kTH1AFN02000,; Liebert EXS,0020kTH1AFN02000, | Ac-output UPS | Static | 0020kTH1AFN01000 | 20000 | 20000 | 0020kTH1AFN01000 |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 415-415 | 60-60 | 240-415 | 60-60 | No |  | 1300 | 335 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 101.65 |  | 94.9 |  | 95.8 |  | 95.7 |  | 95.4 |  | 95.5 | [8 empty] | 0.99 | [22 empty] | 95.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | Determined by customer | Determined by customer | Determined by customer | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | http://www.emersonnetworkpower.com/en-US/Products/ACPower/Pages/default.aspx | N/A | 2017-10-20 | 2017-09-01 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_0020kTH1AFN01000_09112017103759_6279692
2292536 | Vertiv Corporation | Liebert | ITA-20k00AL3A02P00 | ITA-20k00AL3A02P00 | ITA-10k00AL3A02E00,ITA-10k00AL3A02E00,; ITA-15k00AL3A02E00,ITA-15k00AL3A02E00,; ITA-16k00AE3A02C00,ITA-16k00AE3A02C00,; ITA-16k00AE3A02P00,ITA-16k00AE3A02P00,; ITA-16k00AL3A02C00,ITA-16k00AL3A02C00,; ITA-16k00AL3A02P00,ITA-16k00AL3A02P00,; ITA-20k00AE3A02C00,ITA-20k00AE3A02C00,; ITA-20k00AE3A02P00,ITA-20k00AE3A02P00,; ITA-20k00AL3A02C00,ITA-20k00AL3A02C00,; ITA-20k00AL3A02E00,ITA-20k00AL3A02E00, | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5.5 | 15 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_10978707_ITA-20k00AL3A02P00_03162017020015_9615268
2292537 | Vertiv Corporation | Liebert | ITA-20k00AL3A02C00 | ITA-20k00AL3A02C00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5.5 | 15 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-20k00AL3A02C00_03162017023359_1639990
2292538 | Vertiv Corporation | Liebert | ITA-20k00AE3A02P00 | ITA-20k00AE3A02P00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5.5 | 15 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-20k00AE3A02P00_03162017024710_2430239
2292539 | Vertiv Corporation | Liebert | ITA-20k00AE3A02C00 | ITA-20k00AE3A02C00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5.5 | 15 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-20k00AE3A02C00_03162017025739_3059996
2292540 | Vertiv Corporation | Liebert | ITA-16k00AL3A02P00 | ITA-16k00AL3A02P00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 16000 | 16000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7.5 | 21 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-16k00AL3A02P00_03162017030701_3621067
2292541 | Vertiv Corporation | Liebert | ITA-16k00AL3A02C00 | ITA-16k00AL3A02C00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 16000 | 16000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7.5 | 21 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-16k00AL3A02C00_03162017031657_4217694
2292542 | Vertiv Corporation | Liebert | ITA-16k00AE3A02P00 | ITA-16k00AE3A02P00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 16000 | 16000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7.5 | 21 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-16k00AE3A02P00_03162017033006_5006698
2292543 | Vertiv Corporation | Liebert | ITA-16k00AE3A02C00 | ITA-16k00AE3A02C00 |  | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 16000 | 16000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 7.5 | 21 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2017-03-08 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-16k00AE3A02C00_03162017042623_8383790
2293829 | Vertiv Corporation | Liebert | ITA-06k00AL1102P00 | ITA-06k00AL1102P00 | ITA-05k00AE1102C00,ITA-05k00AE1102C00,; ITA-05k00AE1102P00,ITA-05k00AE1102P00,; ITA-05k00AL1102C00,ITA-05k00AL1102C00,; ITA-05k00AL1102P00,ITA-05k00AL1102P00,; ITA-06k00AE1102C00,ITA-06k00AE1102C00,; ITA-06k00AE1102P00,ITA-06k00AE1102P00,; ITA-06k00AL1102C00,ITA-06k00AL1102C00, | Ac-output UPS | Static | ITA-06k00AL1102P00 | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 400 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 36 |  | 94.7 |  | 95.6 |  | 95.3 |  | 94.9 |  | 95.3 | [8 empty] | 0.99 | [22 empty] | 95.3 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 51.5 | 111.5 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2017-04-09 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-06k00AL1102P00_04102017084631_3991288
2293830 | Vertiv Corporation | Liebert | ITA-10k00ALA102P00 | ITA-10k00ALA102P00 | ITA-10k00AEA102C00,ITA-10k00AEA102C00,; ITA-10k00AEA102P00,ITA-10k00AEA102P00,; ITA-10k00ALA102C00,ITA-10k00ALA102C00, | Ac-output UPS | Static | ITA-10k00AL1102P00 | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 500 |  |  |  | Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 55 |  | 93.9 |  | 95.6 |  | 95.8 |  | 95.2 |  | 95.6 | [8 empty] | 0.95 | [22 empty] | 95.6 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 23.5 | 63.5 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2017-04-09 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA-10k00ALA102P00_04102017084706_4026791
2323917 | Vertiv Corporation | Liebert | Liebert EXS | EXS 0040kTH16FN01000 | Liebert EXS F2 series,EXS 0030kTH16FN01000, | Ac-output UPS | Static | EXS 0040kTH16FN01000 | 40000 | 40000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 1600 | 440 | 749 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 262.6 |  | 95.2 |  | 96.2 |  | 95.7 |  | 95.2 |  | 95.8 | [8 empty] | 0.99 | [22 empty] | 95.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | None | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-05-01 | 2018-08-01 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_EXS 0040kTH16FN01000_08022018105614_7374729
2325036 | Vertiv Corporation | Liebert | Liebert EXS F2 series | 53S20G[C¦Y][0¦6¦7¦8][0¦A¦C¦D¦Q][0¦1¦2¦3¦4¦5¦6¦7¦8¦A¦B¦C¦D¦E][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z] | Liebert EXS F2 series,53S15G[C¦Y][0¦6¦7¦8][0¦A¦C¦D¦Q][0¦1¦2¦3¦4¦5¦6¦7¦8¦A¦B¦C¦D¦E][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z], | Ac-output UPS | Static | 53S20GC000000A0A0A | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 60-60 | 208-220 | 60-60 | No |  | 1600 | 440 | 749 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 163.15 |  | 93.3 |  | 94.1 |  | 93.4 |  | 92.3 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-05-01 | 2018-05-08 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_53S20G[C¦Y][0¦6¦7¦8][0¦A¦C¦D¦Q][0¦1¦2¦3¦4¦_Liebert_08112018070413_1053186
2325105 | Vertiv Corporation | Liebert | Liebert EXS Fr3 series | EXS 0060kTK16FN01000 |  | Ac-output UPS | Static | EXS 0060kTK16FN01000 | 60000 | 60000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 1600 | 600 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 575.06 |  | 94.3 |  | 95.7 |  | 95.8 |  | 95.7 |  | 95.4 | [8 empty] | 0.99 | [22 empty] | 95.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | None | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-09-01 | 2018-08-17 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_EXS 0060kTK16FN01000_08172018065744_9064669
2328733 | Vertiv Corporation | Liebert | GXT5-20KIRT9UXLN | GXT5-20KIRT9UXLN | GXT5-16KIRT9UXLE,GXT5-16KIRT9UXLE,; GXT5-16KIRT9UXLN,GXT5-16KIRT9UXLN,; GXT5-20KIRT9UXLE,GXT5-20KIRT9UXLE, | Ac-output UPS | Static | GXT5-20KIRT9UXLN | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 345-415 | 50-60 | 200-240 | 50-60 | Yes |  | 394 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 84.92 |  | 94.9 |  | 95.8 |  | 95.8 |  | 95.5 |  | 95.6 | [8 empty] | 0.99 | [22 empty] | 95.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 2 | 7 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-20KIRT9UXLN_10312018085936_6376455
2328744 | Vertiv Corporation | Liebert | GXT5-10KIRT5UXLN | GXT5-10KIRT5UXLN | GXT5-10KHVRT5UXLN,GXT5-10KHVRT5UXLN,; GXT5-10KIRT5UXLE,GXT5-10KIRT5UXLE,; GXT5-8000HVRT5UXLN,GXT5-8000HVRT5UXLN,; GXT5-8000IRT5UXLE,GXT5-8000IRT5UXLE,; GXT5-8000IRT5UXLN,GXT5-8000IRT5UXLN, | Ac-output UPS | Static | GXT5-10KIRT5UXLN | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 64.22 |  | 94.7 |  | 95.3 |  | 95.2 |  | 94.8 |  | 95.1 | [8 empty] | 0.99 | [22 empty] | 95.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 2 | 7 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-10KIRT5UXLN_10312018091210_7130713
2328746 | Vertiv Corporation | Liebert | GXT5-6000IRT5UXLN | GXT5-6000IRT5UXLN | GXT5-5000HVRT5UXLN,GXT5-5000HVRT5UXLN,; GXT5-5000IRT5UXLE,GXT5-5000IRT5UXLE,; GXT5-5000IRT5UXLN,GXT5-5000IRT5UXLN,; GXT5-6000IRT5UXLE,GXT5-6000IRT5UXLE, | Ac-output UPS | Static | GXT5-6000IRT5UXLN | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 45.74 |  | 94.1 |  | 95.1 |  | 94.9 |  | 94.6 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 14 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-6000IRT5UXLN_10312018092710_8030766
2328748 | Vertiv Corporation | Liebert | GXT5-6KL630RT5UXLN | GXT5-6KL630RT5UXLN |  | Ac-output UPS | Static | GXT5-6KL630RT5UXLN | 5300 | 5700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 45.45 |  | 93.9 |  | 95 |  | 95 |  | 94.6 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-6KL630RT5UXLN_10312018085252_5972475
2329179 | Vertiv Corporation | Liebert | GXE-06k00TL1102C00 | GXE-06k00TL1102C00 | GXE-06k00TE1102C00,GXE-06k00TE1102C00,; GXE-06k00TE1102P00,GXE-06k00TE1102P00,; GXE-06k00TL1102P00,GXE-06k00TL1102P00, | Ac-output UPS | Static | GXE-06k00TL1102C00 | 5400 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 350 | 160 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 30.3 |  | 94.7 |  | 95.5 |  | 95.5 |  | 95.2 |  | 95.4 | [8 empty] | 0.9 | [22 empty] | 95.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 14 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-06k00TL1102C00_11022018063509_0509444
2329181 | Vertiv Corporation | Liebert | GXE-10k00TLA102C00 | GXE-10k00TLA102C00 | GXE-10k00TEA102C00,GXE-10k00TEA102C00,; GXE-10k00TEA102P00,GXE-10k00TEA102P00,; GXE-10k00TLA102P00,GXE-10k00TLA102P00, | Ac-output UPS | Static | GXE-10k00TLA102C00 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 220-240 | 50-60 | Yes |  | 420 | 160 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 53.1 |  | 94.2 |  | 95.4 |  | 95.6 |  | 95.5 |  | 95.5 | [8 empty] | 0.9 | [22 empty] | 95.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-10k00TLA102C00_11022018065414_1654049
2329183 | Vertiv Corporation | Liebert | GXE-20k00TL3302C00 | GXE-20k00TL3302C00 | GXE-15k00TL3102C00,GXE-15k00TL3102C00,; GXE-15k00TL3102P00,GXE-15k00TL3102P00,; GXE-15k00TL3302C00,GXE-15k00TL3302C00,; GXE-15k00TL3302P00,GXE-15k00TL3302P00,; GXE-20k00TL3102C00,GXE-20k00TL3102C00,; GXE-20k00TL3102P00,GXE-20k00TL3102P00,; GXE-20k00TL3302P00,GXE-20k00TL3302P00, | Ac-output UPS | Static | GXE-20k00TL3302C00 | 18000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 420 | 160 | 530 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 81.7 |  | 95.2 |  | 96.2 |  | 96.2 |  | 96.1 |  | 96 | [8 empty] | 0.9 | [22 empty] | 96 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-20k00TL3302C00_11022018071851_3131671
2331005 | Vertiv Corporation | Liebert | GXT5-3000LVRT2UXL | GXT5-3000LVRT2UXL |  | Ac-output UPS | Static | GXT5-3000LVRT2UXL | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 540 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 41.89 |  | 91.4 |  | 92.5 |  | 92.4 |  | 91.7 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-3000LVRT2UXL_12072018022449_9489992
2331007 | Vertiv Corporation | Liebert | GXT5-2000LVRT2UXL | GXT5-2000LVRT2UXL |  | Ac-output UPS | Static | GXT5-2000LVRT2UXL | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 470 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.83 |  | 90.9 |  | 92.7 |  | 92.4 |  | 92.3 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-2000LVRT2UXL_12072018022514_9514278
2331009 | Vertiv Corporation | Liebert | GXT5-1500LVRT2UXL | GXT5-1500LVRT2UXL |  | Ac-output UPS | Static | GXT5-1500LVRT2UXL | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 470 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 38.69 |  | 87.4 |  | 90.1 |  | 90.9 |  | 90.5 |  | 90.5 | [8 empty] | 0.99 | [22 empty] | 90.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 13 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-1500LVRT2UXL_12072018022540_9540383
2331011 | Vertiv Corporation | Liebert | GXT5-1000LVRT2UXL | GXT5-1000LVRT2UXL | GXT5-750LVRT2UXL,GXT5-750LVRT2UXL, | Ac-output UPS | Static | GXT5-1000LVRT2UXL | 1000 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 26.33 |  | 87.3 |  | 90.5 |  | 90.7 |  | 90.3 |  | 90.5 | [8 empty] | 0.99 | [22 empty] | 90.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 15 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-1000LVRT2UXL_12072018022711_9631677
2331873 | Vertiv Corporation | Liebert | GXT5-6000MVRT4UXLN | GXT5-6000MVRT4UXLN | GXT5-5000MVRT4UXLN,GXT5-5000MVRT4UXLN, | Ac-output UPS | Static | GXT5-6000MVRT4UXLN | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 173 | 430 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.64 |  | 93.6 |  | 94.3 |  | 94 |  | 93.6 |  | 94 | [8 empty] | 1 | [22 empty] | 94 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-30 | 2018-12-20 | United States, Taiwan, Japan, Canada | ES_1097807_GXT5-6000MVRT4UXLN_12212018033950_3590768
2331875 | Vertiv Corporation | Liebert | GXT5-10KMVRT6UXLN | GXT5-10KMVRT6UXLN | GXT5-8000MVRT6UXLN,GXT5-8000MVRT6UXLN, | Ac-output UPS | Static | GXT5-10KMVRT6UXLN | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 261 | 430 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 50.39 |  | 94.4 |  | 94.5 |  | 94 |  | 93 |  | 93.9 | [8 empty] | 1 | [22 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-30 | 2018-12-20 | United States, Taiwan, Japan, Canada | ES_1097807_GXT5-10KMVRT6UXLN_12212018034955_4195833
2331995 | Vertiv Corporation | Liebert | GXT4-6000RT230 | GXT4-6000RT230 | GXT4-6000RT230E,GXT4-6000RT230E, | Ac-output UPS | Static | GXT4-6000RT230 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.24 |  | 91 |  | 94.4 |  | 94 |  | 94 |  | 93.8 | [8 empty] | 0.99 | [22 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RT230_12262018014915_8955191
2332007 | Vertiv Corporation | Liebert | GXT4-5000RT230 | GXT4-5000RT230 | GXT4-5000RT230E,GXT4-5000RT230E,; GXT4-5000RT230U,GXT4-5000RT230U, | Ac-output UPS | Static | GXT4-5000RT230 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.2 |  | 90.2 |  | 93.1 |  | 93.8 |  | 94 |  | 93.6 | [8 empty] | 0.99 | [22 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 9 | 22 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-5000RT230_12262018020433_9873355
2332018 | Vertiv Corporation | Liebert | GXT4-10000RT230 | GXT4-10000RT230 | GXT4-10000RT230E,GXT4-10000RT230E, | Ac-output UPS | Static | GXT4-10000RT230 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 261 | 430 | 581 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 112.6 |  | 93.2 |  | 93.2 |  | 93.3 |  | 93.1 |  | 93.2 | [8 empty] | 0.99 | [22 empty] | 93.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 4 | 10 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-10000RT230_12262018022106_0866638
2332020 | Vertiv Corporation | Liebert | GXT4-5000RT208 | GXT4-5000RT208 |  | Ac-output UPS | Static | GXT4-5000RT208 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 77.7 |  | 88.9 |  | 91.9 |  | 92.6 |  | 92 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-5000RT208_12262018023842_1922710
2332025 | Vertiv Corporation | Liebert | GXT4-6000RT208 | GXT4-6000RT208 |  | Ac-output UPS | Static | GXT4-6000RT208 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 76.6 |  | 90.2 |  | 92.6 |  | 92.9 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 12 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RT208_12262018024655_2415913
2332030 | Vertiv Corporation | Liebert | GXT4-6000RTL630 | GXT4-6000RTL630 |  | Ac-output UPS | Static | GXT4-6000RTL630 | 4200 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 82.7 |  | 89.5 |  | 92.4 |  | 93.2 |  | 93.3 |  | 93 | [8 empty] | 0.99 | [22 empty] | 93 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 20 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RTL630_12262018025719_3039208
2332039 | Vertiv Corporation | Liebert | ITA-06k00AL1102P00 | ITA-06k00AL1102P00 | ITA-05k00AE1102C00,ITA-05k00AE1102C00,; ITA-05k00AE1102P00,ITA-05k00AE1102P00,; ITA-05k00AL1102C00,ITA-05k00AL1102C00,; ITA-05k00AL1102P00,ITA-05k00AL1102P00,; ITA-06k00AE1102C00,ITA-06k00AE1102C00,; ITA-06k00AE1102P00,ITA-06k00AE1102P00,; ITA-06k00AL1102C00,ITA-06k00AL1102C00, | Ac-output UPS | Static | ITA-06k00AL1102P00 | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 36 |  | 94.7 |  | 95.6 |  | 95.3 |  | 94.9 |  | 95.3 | [8 empty] | 0.99 | [22 empty] | 95.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 51 | 111 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2018-12-25 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-06k00AL1102P00_12262018052513_1913042
2332043 | Vertiv Corporation | Liebert | ITA-10k00ALA102P00 | ITA-10k00ALA102P00 | ITA-10k00AEA102C00,ITA-10k00AEA102C00,; ITA-10k00AEA102P00,ITA-10k00AEA102P00,; ITA-10k00ALA102C00,ITA-10k00ALA102C00, | Ac-output UPS | Static | ITA-10k00ALA102P00 | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 55 |  | 93.9 |  | 95.6 |  | 95.8 |  | 95.2 |  | 95.6 | [8 empty] | 0.95 | [22 empty] | 95.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 23 | 63 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2018-12-25 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-10k00ALA102P00_12262018054755_3275409
2332106 | Vertiv Corporation | Liebert | ITA-20k00AL3A02C00 | ITA-20k00AL3A02C00 | ITA-10k00AL3A02E00,ITA-10k00AL3A02E00,; ITA-15k00AL3A02E00,ITA-15k00AL3A02E00,; ITA-16k00AE3A02C00,ITA-16k00AE3A02C00,; ITA-16k00AE3A02P00,ITA-16k00AE3A02P00,; ITA-16k00AL3A02C00,ITA-16k00AL3A02C00,; ITA-16k00AL3A02P00,ITA-16k00AL3A02P00,; ITA-20k00AE3A02C00,ITA-20k00AE3A02C00,; ITA-20k00AE3A02P00,ITA-20k00AE3A02P00,; ITA-20k00AL3A02E00,ITA-20k00AL3A02E00,; ITA-20k00AL3A02P00,ITA-20k00AL3A02P00, | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 15 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2018-12-26 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-20k00AL3A02C00_12272018011634_3394232
2308187 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SN12MA |  | Ac-output UPS | Static | 52SN10MA | 1200000 | 1200000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 3276 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 96.1 | 97.9 | 96.6 | 98.5 | 96.5 | 98.6 | 96.2 | 98.5 | 96.4 | 98.4 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SN12MA_12212017160804_2484824
2308188 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SN11MA |  | Ac-output UPS | Static | 52SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 3276 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.9 | 97.7 | 96.6 | 98.4 | 96.5 | 98.6 | 96.3 | 98.6 | 96.4 | 98.3 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SN11MA_12212017162007_3207541
2308190 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SN10MA |  | Ac-output UPS | Static | 52SN12MA | 1000000 | 1000000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 3276 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.7 | 97.6 | 96.5 | 98.4 | 96.6 | 98.6 | 96.4 | 98.6 | 96.3 | 98.2 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SN10MA_12212017162933_3773950
2308191 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SN900A |  | Ac-output UPS | Static | 52SN12MA | 900000 | 900000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 3276 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.4 | 97.3 | 96.4 | 98.3 | 96.6 | 98.5 | 96.5 | 98.6 | 96.2 | 98.1 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SN900A_12212017163830_4310571
2308194 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SA12MA | EXL S1 Series,52SR12MA, | Ac-output UPS | Static | 52SN10MA | 1200000 | 1200000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 2654 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 96.1 | 97.9 | 96.6 | 98.5 | 96.5 | 98.6 | 96.2 | 98.5 | 96.4 | 98.4 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SA12MA_12212017170050_5650387
2308195 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SA11MA | EXL S1 Series,52SR11MA, | Ac-output UPS | Static | 52SN11MA | 1100000 | 1100000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 2654 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.9 | 97.7 | 96.6 | 98.4 | 96.5 | 98.6 | 96.3 | 98.6 | 96.4 | 98.3 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SA11MA_12212017171201_6321861
2308197 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SA10MA | EXL S1 Series,52SR10MA, | Ac-output UPS | Static | 52SN12MA | 1000000 | 1000000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 2654 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.7 | 97.6 | 96.5 | 98.4 | 96.6 | 98.6 | 96.4 | 98.6 | 96.3 | 98.2 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SA10MA_12212017172657_7217217
2308198 | Vertiv Corporation | Vertiv | EXL S1 Series | 52SA900A | EXL S1 Series,52SR900A, | Ac-output UPS | Static | 52SN12MA | 900000 | 900000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Data Center | 480-480 | 60-60 | 480-480 | 60-60 | No |  | 2009 | 2654 | 914 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 480 | 60 | 480 | 60 | 7669.16 | 5402.2 | 95.4 | 97.3 | 96.4 | 98.3 | 96.6 | 98.5 | 96.5 | 98.6 | 96.2 | 98.1 | [7 empty] | 0.99 | 0.99 | [21 empty] | 96.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | Yes | 10 | 20 | 1 | http://www.enersys.com/ |  | Serial Port,Ethernet | Modbus TCP,Other,HTTP,Modbus RTU | HTTPS, SNMP (v1, 2) | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/liebert-exl-s1/ | N/A | 2017-06-23 | 2017-12-18 | United States, Canada | ES_1097807_52SA900A_12212017173915_7955813
2308708 | Vertiv Corporation | Vertiv | ITA2-10KRT208 | ITA2-10KRT208 | ITA2-08KRT208,ITA2-08KRT208,; ITA2-08KRT208C,ITA2-08KRT208C,; ITA2-10KRT208C,ITA2-10KRT208C, | Ac-output UPS | Static | ITA2-10KRT208 | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 60-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 40 |  | 93.3 |  | 94.2 |  | 93.9 |  | 92.8 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Vented Lead-acid Battery | Separate Enclosure | No | 5.5 | 15 | 2 | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-12-01 | 2017-12-25 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_ITA2-10KRT208_12262017083206_7126882
2310218 | Vertiv Corporation | Vertiv | Liebert EXS | 53S010[A¦B][C¦Y][0¦1¦2¦3¦4][000¦BD0¦CC0¦CC1¦CD0¦CE0¦AD0¦FC0¦FC1¦FC3¦FD2¦FD1¦FD3¦JC1¦JD0¦KD0¦MD0¦ND2¦][0-9¦A-Z] [0-9¦A-Z] [0-9¦A-Z] [0¦1¦4¦5¦6¦9¦A¦B¦C] [0-9¦A-Z] [0¦A¦B¦C][0-9¦A-Z] [0¦1][0¦1]0[0-9¦A-Z] [0-9¦A-Z] [0-9¦A-Z] | Liebert EXS,53S008[A¦B][C¦Y][0¦1¦2¦3¦4][000¦BD0¦CC0¦CC1¦CD0¦CE0¦AD0¦FC0¦FC1¦FC3¦FD2¦FD1¦FD3¦JC1¦JD0¦KD0¦MD0¦ND2¦][0-9¦A-Z] [0-9¦A-Z] [0-9¦A-Z] [0¦1¦4¦5¦6¦9¦A¦B¦C] [0-9¦A-Z] [0¦A¦B¦C][0-9¦A-Z] [0¦1][0¦1]0[0-9¦A-Z] [0-9¦A-Z] [0-9¦A-Z], | Ac-output UPS | Static | 53SA010AC10000000000000000 | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1300 | 334 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 79.27 |  | 92.4 |  | 93.4 |  | 93.1 |  | 92.5 |  | 93 | [8 empty] | 0.99 | [22 empty] | 93 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-02-01 | 2018-02-06 | United States, Australia, New Zealand, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_53SA010_02082018024937_8177922
2315192 | Vertiv Corporation | Vertiv | PSA5-1500MT120 | PSA5-1500MT120 |  | Ac-output UPS | Static | PSA5-1500MT120 | 900 | 1440 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 101 | 406 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.59 |  | 97.7 |  | 98 |  | 98.2 |  | 98 |  | 98 | [8 empty] | 0.99 | [22 empty] | 98 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-05-01 | 2018-03-28 | United States, Canada | ES_1097807_PSA5-1500MT120_03012018011437_2994705
2316644 | Vertiv Corporation | Vertiv | PSA5-500MT120 | PSA5-500MT120 |  | Ac-output UPS | Static | PSA5-500MT120 | 300 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.06 |  | 93.5 |  | 96.5 |  | 97.4 |  | 97.8 |  | 97.2 | [8 empty] | 0.99 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-05-01 | 2018-04-03 | United States, Canada | ES_1097807_PSA5-500MT120_03292018221154_7030390
2316645 | Vertiv Corporation | Vertiv | PSA5-700MT120 | PSA5-700MT120 |  | Ac-output UPS | Static | PSA5-700MT120 | 420 | 700 | PSA5-700MT120 |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.56 |  | 95.6 |  | 97.4 |  | 97.8 |  | 97.9 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-05-01 | 2018-04-03 | United States, Canada | ES_1097807_PSA5-700MT120_03292018062007_9312083
2316646 | Vertiv Corporation | Vertiv | PSA5-1000MT120 | PSA5-1000MT120 |  | Ac-output UPS | Static | PSA5-1000MT120 | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.14 |  | 96.4 |  | 97.8 |  | 98.1 |  | 98 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-05-01 | 2018-04-03 | United States, Canada | ES_1097807_PSA5-1000MT120_03292018060948_7745413
2318181 | Vertiv Corporation | Vertiv | PST5-350MT120 | PST5-350MT120 |  | Ac-output UPS | Static | PST5-350MT120 | 200 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.14 |  | 94.9 |  | 97.2 |  | 97.9 |  | 98.2 |  | 97.2 | [8 empty] | 0.99 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 11 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-06-01 | 2018-04-10 | United States, Canada | ES_1097807_PST5-350MT120_04032018043059_3594064
2318182 | Vertiv Corporation | Vertiv | PST5-500MT120 | PST5-500MT120 |  | Ac-output UPS | Static | PST5-500MT120 | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.67 |  | 96.4 |  | 97.9 |  | 98.4 |  | 98.5 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-06-01 | 2018-04-10 | United States, Canada | ES_1097807_PST5-500MT120_04032018042150_4287069
2318183 | Vertiv Corporation | Vertiv | PST5-660MT120 | PST5-660MT120 |  | Ac-output UPS | Static | PST5-660MT120 | 400 | 660 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.75 |  | 97.1 |  | 98.2 |  | 98.5 |  | 98.5 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-06-01 | 2018-04-10 | United States, Canada | ES_1097807_PST5-660MT120_04032018035759_5992600
2318184 | Vertiv Corporation | Vertiv | PST5-850MT120 | PST5-850MT120 |  | Ac-output UPS | Static | PST5-850MT120 | 500 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.75 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.5 |  | 98.3 | [8 empty] | 0.99 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 1.5 | 11 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-06-01 | 2018-04-10 | United States, Canada | ES_1097807_PST5-850MT120_04032018034416_9590074
2319915 | Vertiv Corporation | Vertiv | PSI5-800RT120 | PSI5-800RT120 | PSI5-800RT120TAA,PSI5-800RT120TAA, | Ac-output UPS | Static | PSI5-800RT120, PSI5-800RT120TAA | 720 | 800 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 88 | 438 | 410 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.3 |  | 96.4 |  | 95.7 |  | 97.7 |  | 97 |  | 96.9 | [8 empty] | 1 | [22 empty] | 96.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-800RT120_05152018114128_7915173
2319916 | Vertiv Corporation | Vertiv | PSI5-1100RT120 | PSI5-1100RT120 | PSI5-1100RT120TAA,PSI5-1100RT120TAA, | Ac-output UPS | Static | PSI5-1100RT120, PSI5-1100RT120TAA | 990 | 1100 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 438 | 410 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.5 |  | 95.7 |  | 97.1 |  | 97.1 |  | 96.9 |  | 97 | [8 empty] | 1 | [22 empty] | 97 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-1100RT120_05152018115312_3631545
2319917 | Vertiv Corporation | Vertiv | PSI5-3000RT120 | PSI5-3000RT120 | PSI5-3000RT120TAA,PSI5-3000RT120TAA, | Ac-output UPS | Static | PSI5-3000RT120, PSI5-3000RT120TAA | 2700 | 2880 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 630 | 438 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 14.3 |  | 97.3 |  | 97.7 |  | 97.9 |  | 97.5 |  | 97.7 | [8 empty] | 1 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-3000RT120_05152018115951_2768038
2319918 | Vertiv Corporation | Vertiv | PSI5-5000RT208 | PSI5-5000RT208 | PSI5-5000RT208TAA,PSI5-5000RT208TAA, | Ac-output UPS | Static | PSI5-5000RT208, PSI5-5000RT208TAA | 4500 | 5000 |  |  |  | Other | ac - Other | Consumer | 200-240 | 50-60 | 200-240 | 50-60 | Yes | 2 | 88 | 630 | 438 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 230 | 60 | 230 | 60 | 14.3 |  | 98 |  | 98.8 |  | 98.8 |  | 98.8 |  | 98.8 | [8 empty] | 1 | [22 empty] | 98.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-5000RT208_05152018120404_9426466
2320182 | Vertiv Corporation | Vertiv | PSI5-1500RT120 | PSI5-1500RT120 | PSI5-1500RT120TAA,PSI5-1500RT120TAA, | Ac-output UPS | Static | PSI5-1500RT120, PSI5-1500RT120TAA | 1350 | 1440 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 510 | 438 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.2 |  | 96.8 |  | 97.4 |  | 97.3 |  | 97.1 |  | 97.3 | [8 empty] | 1 | [22 empty] | 97.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-1500RT120_05212018133733_8828549
2320183 | Vertiv Corporation | Vertiv | PSI5-2200RT120 | PSI5-2200RT120 | PSI5-2200RT120TAA,PSI5-2200RT120TAA, | Ac-output UPS | Static | PSI5-2200RT120, PSI5-2200RT120TAA | 1920 | 1920 |  |  |  | Other | ac - Other | Consumer | 100-125 | 50-60 | 100-125 | 50-60 | Yes | 2 | 88 | 630 | 438 | 8 | 1 | 0 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 12.2 |  | 97 |  | 97.4 |  | 96.8 |  | 96.3 |  | 96.8 | [8 empty] | 1 | [22 empty] | 96.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | No | 5 min | 10 min | 3 | N/A |  | Serial Port,USB Port,Ethernet | None |  | Yes |  | www.VertivCo.com | N/A | 2018-03-15 | 2018-05-14 | United States, Canada | ES_1097807_PSI5-2200RT120_05212018134201_7408919
2320752 | Vertiv Corporation | Vertiv | Liebert EXS | EXS 0040KTH16FN01000 | Liebert EXS,EXS 0030KTH16FN01000, | Ac-output UPS | Static | EXS 0040KTH16FN01000 | 40000 | 40000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 1600 | 440 | 749 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 262.6 |  | 95.2 |  | 96.2 |  | 95.7 |  | 95.2 |  | 95.8 | [8 empty] | 0.99 | [22 empty] | 95.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-05-01 | 2018-05-08 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_EXS 0040KTH16FN01000_06012018154555_7955839
2320753 | Vertiv Corporation | Vertiv | Liebert EXS F2 series | 53S20G[C¦Y][0¦6¦7¦8][0¦A¦C¦D¦Q][0¦1¦2¦3¦4¦5¦6¦7¦8¦A¦B¦C¦D¦E][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z] | Liebert EXS F2 series,53S15G[C¦Y][0¦6¦7¦8][0¦A¦C¦D¦Q][0¦1¦2¦3¦4¦5¦6¦7¦8¦A¦B¦C¦D¦E][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0¦A¦B¦C¦1¦2¦3¦4¦5¦6¦7¦8¦9¦W¦X¦Y][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z], | Ac-output UPS | Static | 53S20GC000000A0A0A | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 60-60 | 208-220 | 60-60 | No |  | 1600 | 440 | 749 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 163.15 |  | 93.3 |  | 94.1 |  | 93.4 |  | 92.3 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-05-01 | 2018-05-08 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_53S20G_06012018155330_8410864
2322574 | Vertiv Corporation | Vertiv | PST5-850MT120TAA | PST5-850MT120TAA |  | Ac-output UPS | Static | PST5-850MT120TAA | 500 | 850 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.75 |  | 97.7 |  | 98.5 |  | 98.6 |  | 98.5 |  | 98.3 | [8 empty] | 0.99 | [22 empty] | 98.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 1.5 | 11 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PST5-850MT120TAA_07092018050300_5379660
2322575 | Vertiv Corporation | Vertiv | PST5-660MT120TAA | PST5-660MT120TAA |  | Ac-output UPS | Static | PST5-660MT120TAA | 400 | 660 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.75 |  | 97.1 |  | 98.2 |  | 98.5 |  | 98.5 |  | 98.1 | [8 empty] | 0.99 | [22 empty] | 98.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PST5-660MT120TAA_07092018050051_4916494
2322576 | Vertiv Corporation | Vertiv | PST5-500MT120TAA | PST5-500MT120TAA |  | Ac-output UPS | Static | PST5-500MT120TAA | 300 | 500 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 2.67 |  | 96.4 |  | 97.9 |  | 98.4 |  | 98.5 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 9 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PST5-500MT120TAA_07092018045759_4034836
2322577 | Vertiv Corporation | Vertiv | PST5-350MT120TAA | PST5-350MT120TAA |  | Ac-output UPS | Static | PST5-350MT120TAA | 200 | 350 |  |  |  | Passive Standby | Alternating Current (ac) - Offline (VFD) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 97 | 305 | 158 | 8 | 8 | 4 | Voltage and Frequency Dependent | No | Single-normal-mode | Voltage and Frequency Dependent | 120 | 60 | 120 | 60 | 4.14 |  | 94.9 |  | 97.2 |  | 97.9 |  | 98.2 |  | 97.2 | [8 empty] | 0.99 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 11 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PST5-350MT120TAA_07092018045125_9896202
2322579 | Vertiv Corporation | Vertiv | PSA5-1000MT120TAA | PSA5-1000MT120TAA |  | Ac-output UPS | Static | PSA5-1000MT120TAA | 600 | 1000 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.14 |  | 96.4 |  | 97.8 |  | 98.1 |  | 98 |  | 97.9 | [8 empty] | 0.99 | [22 empty] | 97.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 7 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PSA5-1000MT120TAA_07082018231532_3766284
2322580 | Vertiv Corporation | Vertiv | PSA5-700MT120TAA | PSA5-700MT120TAA |  | Ac-output UPS | Static | PSA5-700MT120TAA | 420 | 700 | PSA5-700MT120TAA |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 4.56 |  | 95.6 |  | 97.4 |  | 97.8 |  | 97.9 |  | 97.7 | [8 empty] | 0.99 | [22 empty] | 97.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PSA5-700MT120TAA_07082018231320_7885780
2322581 | Vertiv Corporation | Vertiv | PSA5-500MT120TAA | PSA5-500MT120TAA |  | Ac-output UPS | Static | PSA5-500MT120TAA | 300 | 500 |  |  |  | Line Interactive | ac Line Interactive (VI) | Consumer | 120-120 | 50-60 | 120-120 | 50-60 | No |  | 279 | 87 | 288 | 10 | 10 | 5 | Voltage Independent | No | Single-normal-mode | Voltage Independent | 120 | 60 | 120 | 60 | 5.06 |  | 93.5 |  | 96.5 |  | 97.4 |  | 97.8 |  | 97.2 | [8 empty] | 0.99 | [22 empty] | 97.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | 2 | 8 | 1 | https://www.vertivco.com/en-us/support/ |  | USB Port | None |  | No |  | https://www.vertivco.com/en-us/support/ | N/A | 2018-10-01 | 2018-07-12 | United States, Canada | ES_1097807_PSA5-500MT120TAA_07082018224927_5871083
2323916 | Vertiv Corporation | Vertiv | Liebert EXS | EXS 0040kTH16FN01000 | Liebert EXS F2 series,EXS 0030kTH16FN01000, | Ac-output UPS | Static | EXS 0040kTH16FN01000 | 40000 | 40000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 1600 | 440 | 749 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 262.6 |  | 95.2 |  | 96.2 |  | 95.7 |  | 95.2 |  | 95.8 | [8 empty] | 0.99 | [22 empty] | 95.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | None | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-05-01 | 2018-08-01 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_EXS 0040kTH16FN01000_08022018105124_7084359
2323918 | Vertiv Corporation | Vertiv | Liebert EXS F3 series | 53[S¦P]30H[C¦Y][0¦E¦F][0¦B¦E¦F¦H¦J¦K¦L¦M¦N¦P¦R][0-8¦A-E][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z][0-9¦A-Z] |  | Ac-output UPS | Static | 53S30HC00000000 | 30000 | 30000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-220 | 60-60 | 208-220 | 60-60 | No |  | 1600 | 600 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 341.45 |  | 92.4 |  | 94.1 |  | 93.9 |  | 93.4 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | Serial Port,USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-08-14 | 2018-08-01 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_53[S¦P]30H[C¦Y][0¦E¦F]_08022018085512_0112423
2325104 | Vertiv Corporation | Vertiv | Liebert EXS Fr3 series | EXS 0060kTK16FN01000 |  | Ac-output UPS | Static | EXS 0060kTK16FN01000 | 60000 | 60000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | No |  | 1600 | 600 | 850 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 575.06 |  | 94.3 |  | 95.7 |  | 95.8 |  | 95.7 |  | 95.4 | [8 empty] | 0.99 | [22 empty] | 95.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 10 | 20 | 1 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | None | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-09-01 | 2018-08-17 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_EXS 0060kTK16FN01000_08172018065600_8960926
2328743 | Vertiv Corporation | Vertiv | GXT5-20KIRT9UXLN | GXT5-20KIRT9UXLN | GXT5-16KIRT9UXLE,GXT5-16KIRT9UXLE,; GXT5-16KIRT9UXLN,GXT5-16KIRT9UXLN,; GXT5-20KIRT9UXLE,GXT5-20KIRT9UXLE, | Ac-output UPS | Static | GXT5-20KIRT9UXLN | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 345-415 | 50-60 | 200-240 | 50-60 | Yes |  | 394 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 84.92 |  | 94.9 |  | 95.8 |  | 95.8 |  | 95.5 |  | 95.6 | [8 empty] | 0.99 | [22 empty] | 95.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 2 | 7 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-20KIRT9UXLN_10312018085432_6072391
2328745 | Vertiv Corporation | Vertiv | GXT5-10KIRT5UXLN | GXT5-10KIRT5UXLN | GXT5-10KHVRT5UXLN,GXT5-10KHVRT5UXLN,; GXT5-10KIRT5UXLE,GXT5-10KIRT5UXLE,; GXT5-8000HVRT5UXLN,GXT5-8000HVRT5UXLN,; GXT5-8000IRT5UXLE,GXT5-8000IRT5UXLE,; GXT5-8000IRT5UXLN,GXT5-8000IRT5UXLN, | Ac-output UPS | Static | GXT5-10KIRT5UXLN | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 64.22 |  | 94.7 |  | 95.3 |  | 95.2 |  | 94.8 |  | 95.1 | [8 empty] | 0.99 | [22 empty] | 95.1 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 2 | 7 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-10KIRT5UXLN_10312018091128_7088320
2328747 | Vertiv Corporation | Vertiv | GXT5-6000IRT5UXLN | GXT5-6000IRT5UXLN | GXT5-5000HVRT5UXLN,GXT5-5000HVRT5UXLN,; GXT5-5000IRT5UXLE,GXT5-5000IRT5UXLE,; GXT5-5000IRT5UXLN,GXT5-5000IRT5UXLN,; GXT5-6000IRT5UXLE,GXT5-6000IRT5UXLE, | Ac-output UPS | Static | GXT5-6000IRT5UXLN | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 45.74 |  | 94.1 |  | 95.1 |  | 94.9 |  | 94.6 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 14 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-6000IRT5UXLN_10312018092650_8010854
2328749 | Vertiv Corporation | Vertiv | GXT5-6KL630RT5UXLN | GXT5-6KL630RT5UXLN |  | Ac-output UPS | Static | GXT5-6KL630RT5UXLN | 5300 | 5700 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 217 | 430 | 630 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 45.45 |  | 93.9 |  | 95 |  | 95 |  | 94.6 |  | 94.9 | [8 empty] | 0.99 | [22 empty] | 94.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-10-31 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-6KL630RT5UXLN_10312018085115_5875236
2329180 | Vertiv Corporation | Vertiv | GXE-06k00TL1102C00 | GXE-06k00TL1102C00 | GXE-06k00TE1102C00,GXE-06k00TE1102C00,; GXE-06k00TE1102P00,GXE-06k00TE1102P00,; GXE-06k00TL1102P00,GXE-06k00TL1102P00, | Ac-output UPS | Static | GXE-06k00TL1102C00 | 5400 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 350 | 160 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 30.3 |  | 94.7 |  | 95.5 |  | 95.5 |  | 95.2 |  | 95.4 | [8 empty] | 0.9 | [22 empty] | 95.4 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 14 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-06k00TL1102C00_11022018063403_0443792
2329182 | Vertiv Corporation | Vertiv | GXE-10k00TLA102C00 | GXE-10k00TLA102C00 | GXE-10k00TEA102C00,GXE-10k00TEA102C00,; GXE-10k00TEA102P00,GXE-10k00TEA102P00,; GXE-10k00TLA102P00,GXE-10k00TLA102P00, | Ac-output UPS | Static | GXE-10k00TLA102C00 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 220-240 | 50-60 | Yes |  | 420 | 160 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 53.1 |  | 94.2 |  | 95.4 |  | 95.6 |  | 95.5 |  | 95.5 | [8 empty] | 0.9 | [22 empty] | 95.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-10k00TLA102C00_11022018065303_1583376
2329184 | Vertiv Corporation | Vertiv | GXE-20k00TL3302C00 | GXE-20k00TL3302C00 | GXE-15k00TL3102C00,GXE-15k00TL3102C00,; GXE-15k00TL3102P00,GXE-15k00TL3102P00,; GXE-15k00TL3302C00,GXE-15k00TL3302C00,; GXE-15k00TL3302P00,GXE-15k00TL3302P00,; GXE-20k00TL3102C00,GXE-20k00TL3102C00,; GXE-20k00TL3102P00,GXE-20k00TL3102P00,; GXE-20k00TL3302P00,GXE-20k00TL3302P00, | Ac-output UPS | Static | GXE-20k00TL3302C00 | 18000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 420 | 160 | 530 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 81.7 |  | 95.2 |  | 96.2 |  | 96.2 |  | 96.1 |  | 96 | [8 empty] | 0.9 | [22 empty] | 96 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 19 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-11-02 | United States, Switzerland, Europe, Taiwan, Japan, Canada | ES_1097807_GXE-20k00TL3302C00_11022018071801_3081007
2331006 | Vertiv Corporation | Vertiv | GXT5-3000LVRT2UXL | GXT5-3000LVRT2UXL |  | Ac-output UPS | Static | GXT5-3000LVRT2UXL | 2700 | 3000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 540 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 41.89 |  | 91.4 |  | 92.5 |  | 92.4 |  | 91.7 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-3000LVRT2UXL_12072018022158_9318539
2331008 | Vertiv Corporation | Vertiv | GXT5-2000LVRT2UXL | GXT5-2000LVRT2UXL |  | Ac-output UPS | Static | GXT5-2000LVRT2UXL | 1800 | 2000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 470 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 27.83 |  | 90.9 |  | 92.7 |  | 92.4 |  | 92.3 |  | 92.5 | [8 empty] | 0.99 | [22 empty] | 92.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-2000LVRT2UXL_12072018022221_9341777
2331010 | Vertiv Corporation | Vertiv | GXT5-1500LVRT2UXL | GXT5-1500LVRT2UXL |  | Ac-output UPS | Static | GXT5-1500LVRT2UXL | 1350 | 1500 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 470 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 38.69 |  | 87.4 |  | 90.1 |  | 90.9 |  | 90.5 |  | 90.5 | [8 empty] | 0.99 | [22 empty] | 90.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 13 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-1500LVRT2UXL_12072018022242_9362277
2331012 | Vertiv Corporation | Vertiv | GXT5-1000LVRT2UXL | GXT5-1000LVRT2UXL | GXT5-750LVRT2UXL,GXT5-750LVRT2UXL, | Ac-output UPS | Static | GXT5-1000LVRT2UXL | 1000 | 1000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 110-125 | 50-60 | 110-125 | 50-60 | Yes |  | 85 | 430 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 26.33 |  | 87.3 |  | 90.5 |  | 90.7 |  | 90.3 |  | 90.5 | [8 empty] | 0.99 | [22 empty] | 90.5 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 6 | 15 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-01 | 2018-12-06 | United States, Europe, Taiwan, Japan, Canada | ES_1097807_GXT5-1000LVRT2UXL_12072018022329_9409271
2331874 | Vertiv Corporation | Vertiv | GXT5-6000MVRT4UXLN | GXT5-6000MVRT4UXLN | GXT5-5000MVRT4UXLN,GXT5-5000MVRT4UXLN, | Ac-output UPS | Static | GXT5-6000MVRT4UXLN | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 173 | 430 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 43.64 |  | 93.6 |  | 94.3 |  | 94 |  | 93.6 |  | 94 | [8 empty] | 1 | [22 empty] | 94 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-30 | 2018-12-20 | United States, Taiwan, Japan, Canada | ES_1097807_GXT5-6000MVRT4UXLN_12212018033503_3303408
2331876 | Vertiv Corporation | Vertiv | GXT5-10KMVRT6UXLN | GXT5-10KMVRT6UXLN | GXT5-8000MVRT6UXLN,GXT5-8000MVRT6UXLN, | Ac-output UPS | Static | GXT5-10KMVRT6UXLN | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 100-125 | 50-60 | 100-125 | 50-60 | Yes |  | 261 | 430 | 650 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 120 | 60 | 120 | 60 | 50.39 |  | 94.4 |  | 94.5 |  | 94 |  | 93 |  | 93.9 | [8 empty] | 1 | [22 empty] | 93.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 3 | 9 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2018-12-30 | 2018-12-20 | United States, Taiwan, Japan, Canada | ES_1097807_GXT5-10KMVRT6UXLN_12212018034849_4129784
2331996 | Vertiv Corporation | Vertiv | GXT4-6000RT230 | GXT4-6000RT230 | GXT4-6000RT230E,GXT4-6000RT230E, | Ac-output UPS | Static | GXT4-6000RT230 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.24 |  | 91 |  | 94.4 |  | 94 |  | 94 |  | 93.8 | [8 empty] | 0.99 | [22 empty] | 93.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RT230_12262018014818_8898742
2332008 | Vertiv Corporation | Vertiv | GXT4-5000RT230 | GXT4-5000RT230 | GXT4-5000RT230E,GXT4-5000RT230E,; GXT4-5000RT230U,GXT4-5000RT230U, | Ac-output UPS | Static | GXT4-5000RT230 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 76.2 |  | 90.2 |  | 93.1 |  | 93.8 |  | 94 |  | 93.6 | [8 empty] | 0.99 | [22 empty] | 93.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 9 | 22 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-5000RT230_12262018020304_9784609
2332019 | Vertiv Corporation | Vertiv | GXT4-10000RT230 | GXT4-10000RT230 | GXT4-10000RT230E,GXT4-10000RT230E, | Ac-output UPS | Static | GXT4-10000RT230 | 9000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 261 | 430 | 581 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 112.6 |  | 93.2 |  | 93.2 |  | 93.3 |  | 93.1 |  | 93.2 | [8 empty] | 0.99 | [22 empty] | 93.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 4 | 10 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-10000RT230_12262018021929_0769890
2332021 | Vertiv Corporation | Vertiv | GXT4-5000RT208 | GXT4-5000RT208 |  | Ac-output UPS | Static | GXT4-5000RT208 | 4000 | 5000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 77.7 |  | 88.9 |  | 91.9 |  | 92.6 |  | 92 |  | 92.2 | [8 empty] | 0.99 | [22 empty] | 92.2 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 7 | 17 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-5000RT208_12262018023826_1906729
2332026 | Vertiv Corporation | Vertiv | GXT4-6000RT208 | GXT4-6000RT208 |  | Ac-output UPS | Static | GXT4-6000RT208 | 4800 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 200-240 | 50-60 | 200-240 | 50-60 | Yes |  | 173 | 430 | 662 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 76.6 |  | 90.2 |  | 92.6 |  | 92.9 |  | 92.8 |  | 92.8 | [8 empty] | 0.99 | [22 empty] | 92.8 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 12 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RT208_12262018024720_2440550
2332031 | Vertiv Corporation | Vertiv | GXT4-6000RTL630 | GXT4-6000RTL630 |  | Ac-output UPS | Static | GXT4-6000RTL630 | 4200 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 208-240 | 50-60 | 208-240 | 50-60 | Yes |  | 217 | 430 | 574 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 82.7 |  | 89.5 |  | 92.4 |  | 93.2 |  | 93.3 |  | 93 | [8 empty] | 0.99 | [22 empty] | 93 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 8 | 20 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2014-03-31 | 2018-12-24 | United States, Taiwan, Japan, Canada | ES_1097807_GXT4-6000RTL630_12262018025701_3021742
2332040 | Vertiv Corporation | Vertiv | ITA-06k00AL1102P00 | ITA-06k00AL1102P00 | ITA-05k00AE1102C00,ITA-05k00AE1102C00,; ITA-05k00AE1102P00,ITA-05k00AE1102P00,; ITA-05k00AL1102C00,ITA-05k00AL1102C00,; ITA-05k00AL1102P00,ITA-05k00AL1102P00,; ITA-06k00AE1102C00,ITA-06k00AE1102C00,; ITA-06k00AE1102P00,ITA-06k00AE1102P00,; ITA-06k00AL1102C00,ITA-06k00AL1102C00, | Ac-output UPS | Static | ITA-06k00AL1102P00 | 6000 | 6000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 220-240 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 400 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 240 | 60 | 240 | 60 | 36 |  | 94.7 |  | 95.6 |  | 95.3 |  | 94.9 |  | 95.3 | [8 empty] | 0.99 | [22 empty] | 95.3 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 51 | 111 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2018-12-25 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-06k00AL1102P00_12262018052017_1617221
2332044 | Vertiv Corporation | Vertiv | ITA-10k00ALA102P00 | ITA-10k00ALA102P00 | ITA-10k00AEA102C00,ITA-10k00AEA102C00,; ITA-10k00AEA102P00,ITA-10k00AEA102P00,; ITA-10k00ALA102C00,ITA-10k00ALA102C00, | Ac-output UPS | Static | ITA-10k00ALA102P00 | 10000 | 10000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 220-240 | 50-60 | Yes |  | 85 | 430 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 240 | 60 | 55 |  | 93.9 |  | 95.6 |  | 95.8 |  | 95.2 |  | 95.6 | [8 empty] | 0.95 | [22 empty] | 95.6 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 23 | 63 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-04-20 | 2018-12-25 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-10k00ALA102P00_12262018054426_3066139
2332107 | Vertiv Corporation | Vertiv | ITA-20k00AL3A02C00 | ITA-20k00AL3A02C00 | ITA-10k00AL3A02E00,ITA-10k00AL3A02E00,; ITA-15k00AL3A02E00,ITA-15k00AL3A02E00,; ITA-16k00AE3A02C00,ITA-16k00AE3A02C00,; ITA-16k00AE3A02P00,ITA-16k00AE3A02P00,; ITA-16k00AL3A02C00,ITA-16k00AL3A02C00,; ITA-16k00AL3A02P00,ITA-16k00AL3A02P00,; ITA-20k00AE3A02C00,ITA-20k00AE3A02C00,; ITA-20k00AE3A02P00,ITA-20k00AE3A02P00,; ITA-20k00AL3A02E00,ITA-20k00AL3A02E00,; ITA-20k00AL3A02P00,ITA-20k00AL3A02P00, | Ac-output UPS | Static | ITA-20k00AL3A02C00 | 20000 | 20000 |  |  |  | Multi-Mode Double Conversion | ac - Other | Commercial,Consumer,Data Center | 380-415 | 50-60 | 380-415 | 50-60 | Yes |  | 130 | 430 | 500 |  |  |  | Voltage and Frequency Dependent,Voltage and Frequency Independent | No | Multiple-normal-mode | Voltage and Frequency Independent | 415 | 60 | 415 | 60 | 88 |  | 95.3 |  | 96.2 |  | 96.1 |  | 96 |  | 95.9 | [8 empty] | 0.99 | [22 empty] | 95.9 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | 5 | 15 | 2 | http://www.enersys.com/ http://www.eastpennunigy.com/ |  | USB Port,Ethernet | Other |  | No |  | https://www.vertivco.com/en-us/products-catalog/critical-power/uninterruptible-power-supplies-ups/ | N/A | 2017-03-20 | 2018-12-26 | United States, Taiwan, Japan, Canada | ES_1097807_ITA-20k00AL3A02C00_12272018011037_3037225
2292399 | XPC Corporation | Xtreme Power Conversion Corp. | M90-ENC | M90-ENC |  | Ac-output UPS | Static | M90-ENC | 54000 | 60000 |  |  |  | Other | ac - Other | Commercial,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 760 | 515 | 1000 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 1294 |  | 92.7 |  | 94.1 |  | 94 |  | 93.4 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Separate Enclosure | No | N/A | N/A | N/A | N/A |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | Yes |  | http://www.xpcc.com/ | N/A | 2017-05-01 | 2017-03-10 | United States, Canada | ES_1138742_M90-ENC_03132017122604_1451779
2292400 | XPC Corporation | Xtreme Power Conversion Corp. | M90L-ENC | M90L-ENC |  | Ac-output UPS | Static | M90L-ENC | 54000 | 60000 |  |  |  | Other | ac - Other | Commercial,Data Center | 208-220 | 50-60 | 208-220 | 50-60 | No |  | 1420 | 515 | 1000 |  |  |  | Voltage and Frequency Independent | No | Single-normal-mode | Voltage and Frequency Independent | 208 | 60 | 208 | 60 | 1294 |  | 92.7 |  | 94.1 |  | 94 |  | 93.4 |  | 93.7 | [8 empty] | 0.99 | [22 empty] | 93.7 | N/A | Battery | Valve Regulated Lead-acid Battery | Integral | N/A | N/A | N/A | N/A | N/A |  | Serial Port,USB Port,Ethernet | SNMP (v1, 2 or 3) |  | Yes |  | http://www.xpcc.com/ | N/A | 2017-05-01 | 2017-03-10 | United States, Canada | ES_1138742_M90L-ENC_03132017123459_7707216